## Modbus File
EcoStruxure Panel Server
Modbus File
Wireless Concentrator and Modbus Gateway, Datalogger and Energy Server
EcoStruxure offers IoT-enabled architecture and platform.
DOCA0241EN-16
07/2026

## Safety Information
Safety Information
Important Information
Read these instructions carefully, and look at the equipment to become familiar with the device before trying to install, operate, service, or maintain it. The following special messages may appear throughout this documentation or on the equipment to warn of potential hazards or to call attention to information that clarifies or simplifies a procedure.
The addition of this symbol to a “Danger” or “Warning” safety label indicates that an electrical hazard exists which will result in personal injury if the instructions are not followed.
This is the safety alert symbol. It is used to alert you to potential personal injury hazards. Obey all safety messages that follow this symbol to avoid possible injury or death.
Please Note
Electrical equipment should be installed, operated, serviced, and maintained only by qualified personnel. No responsibility is assumed by Schneider Electric for any consequences arising out of the use of this material.
A qualified person is one who has skills and knowledge related to the construction and operation of electrical equipment and its installation, and has received safety training to recognize and avoid the hazards involved.

## About the File
About the File
Document Scope
The aim of this file is to provide users, installers, and maintenance personnel with the Modbus registers of: • EcoStruxure™ Panel Server gateways • The wireless devices connected to the Panel Server. These registers provide metering, monitoring, and diagnosis information. For the EcoStruxure Panel Server and each device connected, the list of Modbus registers depends on the application, the type of device and the enabled functions.
Validity Note
This file applies to the following EcoStruxure Panel Server models: • Entry with firmware version 002.007.000 or greater • Universal with firmware version 002.007.000 or greater • Advanced with firmware version 002.007.000 or greater
Online Information
The information contained in this file is likely to be updated at any time. Schneider Electric strongly recommends that you have the most recent and up-to-date version available on www.se.com
The technical characteristics of the devices described in this file also appear online. To access the information online, go to the Schneider Electric home page at www.se.com
Convention
EcoStruxure Panel Server is referred to as Panel Server.
General Cybersecurity Information
In recent years, the growing number of networked machines and production plants has seen a corresponding increase in the potential for cyber threats, such as unauthorized access, data breaches, and operational disruptions. You must, therefore, consider all possible cybersecurity measures to help protect assets and systems against such threats.
To help keep your Schneider Electric products secure and protected, it is in your best interest to implement the cybersecurity best practices as described in the Cybersecurity Best Practices document.
Schneider Electric provides additional information and assistance: • Subscribe to the Schneider Electric security newsletter. • Visit the Cybersecurity Support Portal web page to: • Find Security Notifications. • Report vulnerabilities and incidents. • Visit the Schneider Electric Cybersecurity and Data Protection Posture web page to: • Access the cybersecurity posture. • Learn more about cybersecurity in the cybersecurity academy. • Explore the cybersecurity services from Schneider Electric.
Product Related Cybersecurity Information
FCC Notice
This device complies with Part 15 of the FCC Rules. Operation is subject to the following two conditions: • This device may not cause harmful interference, and • this device must accept any interference received, including interference that may cause undesired operation. NOTE: This equipment has been tested and found to comply with the limits for a Class A digital device, pursuant to part 15 of the FCC Rules. These limits are designed to provide reasonable protection against harmful interference when the equipment is operating in a commercial environment. This equipment generates, uses, and can radiate radiofrequency energy and, if not installed and used in accordance with the instruction manual, may cause harmful interference to radio communications. Operation of this equipment in a residential area is likely to cause harmful interference in which case the user will be required to correct the interference at his own expense. FCC Caution: Any changes or modifications not expressly approved by the party responsible for compliance could void the user’s authority to operate this equipment. This transmitter must not be co-located or operating in conjunction with any other antenna or transmitter. Radiation Exposure Statement: This equipment complies with FCC radiation exposure limits set forth for an uncontrolled environment. This equipment should be installed and operated with minimum distance 20 cm between the radiator and your body. NOTE: The country code selection is for non-US model only and is not available to all US models. Per FCC regulation, all Wi-Fi product marketed in US must fixed to US operation channels only.
Related Documents
| Title of documentation | Reference number
| EcoStruxure Panel Server - User Guide | DOCA0172EN
DOCA0172DE
DOCA0172ES
DOCA0172FR
DOCA0172IT
DOCA0172PT
| EcoStruxure Panel Server Entry - Firmware Release Notes | DOCA0249EN
DOCA0249DE
DOCA0249ES
DOCA0249FR
DOCA0249IT
DOCA0249PT
| EcoStruxure Panel Server Universal - Firmware Release Notes | DOCA0178EN
DOCA0178DE
DOCA0178ES
DOCA0178FR
DOCA0178IT
DOCA0178PT
| EcoStruxure Panel Server Advanced - Firmware Release Notes | DOCA0248EN
DOCA0248DE
DOCA0248ES
DOCA0248FR
DOCA0248IT
DOCA0248PT
You can download these technical publications and other technical information from our website at www.se.com/ww/en/download
Information on Non-Inclusive or Insensitive Terminology
As a responsible, inclusive company, Schneider Electric is constantly updating its communications and products that contain non-inclusive or insensitive terminology. However, despite these efforts, our content may still contain terms that are deemed inappropriate by some customers.

## Commercial References
Commercial References of Supported Gateways
Commercial reference | Device name |  | Go to tab
PAS400 | EcoStruxure Panel Server Entry 110–277 Vac/Vdc |  | Panel Server
PAS600 | EcoStruxure Panel Server Universal 110–277 Vac/Vdc |  | Panel Server
PAS600L | EcoStruxure Panel Server Universal 24 Vdc |  | Panel Server
PAS600LWD | EcoStruxure Panel Server Universal Wired by Design 24 Vdc |  | Panel Server
PAS600T | EcoStruxure Panel Server Universal 110–240 Vac/Vdc |  | Panel Server
PAS600PWD | EcoStruxure Panel Server Universal Wired by Design PoE (Powered over Ethernet) |  | Panel Server
PAS800 | EcoStruxure Panel Server Advanced 110–277 Vac/Vdc |  | Panel Server
PAS800L | EcoStruxure Panel Server Advanced 24 Vdc |  | Panel Server
PAS800P | EcoStruxure Panel Server Advanced PoE (Powered over Ethernet) |  | Panel Server
Commercial References of Supported Wireless Devices
Commercial reference | Device name | Device family for data models | Go to tab
A9MEM1520 | PowerTag A9 M63 1P+W | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1521 | PowerTag A9 M63 1P+N Top | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1522 | PowerTag A9 M63 1P+N Bottom | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1540 | PowerTag A9 M63 3P | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1541 | PowerTag A9 M63 3P+N Top | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1542 | PowerTag A9 M63 3P+N Bottom | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1543 | PowerTag A9 M63 3P 230V LL | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1560 | PowerTag A9 P63 1P+N Top | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1561 | PowerTag A9 P63 1P+N Top | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1562 | PowerTag A9 P63 1P+N Bottom | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1563 | PowerTag A9 P63 1P+N Bottom RCBO | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1564 | PowerTag A9 F63 1P+N 110V | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1570 | PowerTag A9 F63 3P+N | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1571 | PowerTag A9 P63 3P+N Top | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1572 | PowerTag A9 P63 3P+N Bottom | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1573 | PowerTag A9 F63 3P | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1574 | PowerTag A9 F63 3P+N 110/230V | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1575 | PowerTag A9 F63 3P 480V | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
PLTQO301P | PowerLogic Tag QO 10-30A 1P+N | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
PLTQO601P | PowerLogic Tag QO 35-60A 1P+N | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
PLTQO303P | PowerLogic Tag QO 10-30A 3P | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
PLTQO603P | PowerLogic Tag QO 35-60A 3P | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
PLTQO302P | PowerLogic Tag QO 10-30A 2P | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
PLTQO602P | PowerLogic Tag QO 35-60A 2P | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
LV434020 | PowerTag M250 3P 250A | PowerTag Energy M250 M630 and PowerLogic Tag E-Frame | PTEnergy250_630-PoTag Efram
LV434022 | PowerTag M630 3P 630A | PowerTag Energy M250 M630 and PowerLogic Tag E-Frame | PTEnergy250_630-PoTag Efram
LV434021 | PowerTag M250 3P+N 250A | PowerTag Energy M250 M630 and PowerLogic Tag E-Frame | PTEnergy250_630-PoTag Efram
LV434023 | PowerTag M630 3P+N 630A | PowerTag Energy M250 M630 and PowerLogic Tag E-Frame | PTEnergy250_630-PoTag Efram
PLTE601P | PowerLogic Tag E-Frame 10-60A 1P+N | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
PLTE602P | PowerLogic Tag E-Frame 10-60A 2P | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
PLTE603P | PowerLogic Tag E-Frame 10-60A 3P | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1580 | PowerTag F160 3P/3P+N | PowerTag Energy F160 Rope and PowerLogic Tag Rope | PTE Rope-PoTag Rope
A9MEM1590 | PowerTag Rope 200 A 3P/3P+N | PowerTag Energy F160 Rope and PowerLogic Tag Rope | PTE Rope-PoTag Rope
A9MEM1591 | PowerTag Rope 600 A 3P/3P+N | PowerTag Energy F160 Rope and PowerLogic Tag Rope | PTE Rope-PoTag Rope
A9MEM1592 | PowerTag Rope 1000 A 3P/3P+N | PowerTag Energy F160 Rope and PowerLogic Tag Rope | PTE Rope-PoTag Rope
A9MEM1593 | PowerTag Rope 2000 A 3P/3P+N | PowerTag Energy F160 Rope and PowerLogic Tag Rope | PTE Rope-PoTag Rope
PLTR1203P | PowerLogic Tag Rope 120A 3P | PowerTag Energy F160 Rope and PowerLogic Tag Rope | PTE Rope-PoTag Rope
PLTR6003P | PowerLogic Tag Rope 600A 3P | PowerTag Energy F160 Rope and PowerLogic Tag Rope | PTE Rope-PoTag Rope
PLTR10003P | PowerLogic Tag Rope 1000A 3P | PowerTag Energy F160 Rope and PowerLogic Tag Rope | PTE Rope-PoTag Rope
PLTR20003P | PowerLogic Tag Rope 2000A 3P | PowerTag Energy F160 Rope and PowerLogic Tag Rope | PTE Rope-PoTag Rope
EMS59440 | PowerLogic TH110 wireless thermal sensor | TH110 | TH110
EMS59443 | PowerLogic CL110 wireless environmental sensor | CL110 | CL110
SED-CO2-G-5045 | Wireless CO2 sensor | CO2 sensors | CO2 sensors
SED-TRH-G-5045 | Wireless temperature and humidity sensor | Temperature sensors TRH | Temperature sensors TRH
ZBRTT1 | Wireless environmental sensor | Temperature sensors TRH | Temperature sensors TRH
ESST010B0400 | PowerTag A (EwSenseTemp) | Temperature sensors TRH | Temperature sensors TRH
A9XST114 | PowerTag Ambient wireless temperature sensor | Temperature sensors TRH | Temperature sensors TRH
SMT10020 | PowerLogic HeatTag | PowerLogic HeatTag | PowerLogic HeatTag
SPTH150S | PowerLogic Thermal Tag wireless temperature sensor | Thermal sensor (China-certified devices only) | TH150S
SPTH150M | PowerLogic Thermal Tag wireless temperature sensor | Thermal sensor (China-certified devices only) | TH150M
SPTH200M | PowerLogic Thermal Tag wireless temperature sensor | Thermal sensor (China-certified devices only) | TH200M
A9TAA2625 | Acti9 Active ARC iDT40 1PN 25A | Acti9 Active | Acti9 Active
A9TAA1625 | Acti9 ARC iDT40 1PN 25A | Acti9 Active | Acti9 Active
A9TAA2640 | Acti9 Active ARC iDT40 1PN 40A | Acti9 Active | Acti9 Active
A9TAA1640 | Acti9 ARC iDT40 1PN 40A | Acti9 Active | Acti9 Active
A9TAA2225 | Acti9 Active ARC iC60 2P 25A | Acti9 Active | Acti9 Active
A9TAA1225 | Acti9 ARC iC60 2P 25A | Acti9 Active | Acti9 Active
A9TAA2240 | Acti9 Active ARC iC60 2P 40A | Acti9 Active | Acti9 Active
A9TAA1240 | Acti9 ARC iC60 2P 40A | Acti9 Active | Acti9 Active
A9TAB2625 | Acti9 Active ARC iC40 1PN 25A | Acti9 Active | Acti9 Active
A9TAB1625 | Acti9 ARC iC40 1PN 25A | Acti9 Active | Acti9 Active
A9TAB2640 | Acti9 Active ARC iC40 1PN 40A | Acti9 Active | Acti9 Active
A9TAB1640 | Acti9 ARC iC40 1PN 40A | Acti9 Active | Acti9 Active
A9TAB2225 | Acti9 Active ARC iC60 2P 25A | Acti9 Active | Acti9 Active
A9TAB1225 | Acti9 ARC iC60 2P 25A | Acti9 Active | Acti9 Active
A9TAB2240 | Acti9 Active ARC iC60 2P 40A | Acti9 Active | Acti9 Active
A9TAB1240 | Acti9 ARC iC60 2P 40A | Acti9 Active | Acti9 Active
A9TDEC610 | Acti9 Active iCV40N VigiARC 1PN B10 30mA | Acti9 Active | Acti9 Active
A9TDEC613 | Acti9 Active iCV40N VigiARC 1PN B13 30mA | Acti9 Active | Acti9 Active
A9TDEC616 | Acti9 Active iCV40N VigiARC 1PN B16 30mA | Acti9 Active | Acti9 Active
A9TDFC606 | Acti9 Active iCV40N VigiARC 1PN C6 30mA | Acti9 Active | Acti9 Active
A9TDFC610 | Acti9 Active iCV40N VigiARC 1PN C10 30mA | Acti9 Active | Acti9 Active
A9TDFC613 | Acti9 Active iCV40N VigiARC 1PN C13 30mA | Acti9 Active | Acti9 Active
A9TDFC616 | Acti9 Active iCV40N VigiARC 1PN C16 30mA | Acti9 Active | Acti9 Active
A9TDFC625 | Acti9 Active iCV40N VigiARC 1PN C25 30mA | Acti9 Active | Acti9 Active
A9TDFC632 | Acti9 Active iCV40N VigiARC 1PN C32 30mA | Acti9 Active | Acti9 Active
A9TDFC640 | Acti9 Active iCV40N VigiARC 1PN C40 30mA | Acti9 Active | Acti9 Active
A9TDFD606 | Acti9 Active iCV40N VigiARC 1PN C6 30mA | Acti9 Active | Acti9 Active
A9TDFD610 | Acti9 Active iCV40N VigiARC 1PN C10 30mA | Acti9 Active | Acti9 Active
A9TDFD616 | Acti9 Active iCV40N VigiARC 1PN C16 30mA | Acti9 Active | Acti9 Active
A9TDFD620 | Acti9 Active iCV40N VigiARC 1PN C20 30mA | Acti9 Active | Acti9 Active
A9TDFD625 | Acti9 Active iCV40N VigiARC 1PN C25 30mA | Acti9 Active | Acti9 Active
A9TDFD632 | Acti9 Active iCV40N VigiARC 1PN C32 30mA | Acti9 Active | Acti9 Active
A9TPDD610 | Acti9 Active iC40N ARC 1PN B 10A MCB AFD | Acti9 Active | Acti9 Active
A9TPDD613 | Acti9 Active iC40N ARC 1PN B 13A MCB AFD | Acti9 Active | Acti9 Active
A9TPDD616 | Acti9 Active iC40N ARC 1PN B 16A MCB AFD | Acti9 Active | Acti9 Active
A9TPED610 | Acti9 Active iC40N ARC 1PN C 10A MCB AFD | Acti9 Active | Acti9 Active
A9TPED613 | Acti9 Active iC40N ARC 1PN C 13A MCB AFD | Acti9 Active | Acti9 Active
A9TPED616 | Acti9 Active iC40N ARC 1PN C 16A MCB AFD | Acti9 Active | Acti9 Active
A9TPED625 | Acti9 Active iC40N ARC 1PN C 25A MCB AFD | Acti9 Active | Acti9 Active
A9TPED632 | Acti9 Active iC40 ARC 1PN C 32A MCB AFDD | Acti9 Active | Acti9 Active
A9TPED640 | Acti9 Active iC40N ARC 1PN C 40A MCB AFD | Acti9 Active | Acti9 Active
A9TYAE625 | Acti9 VigiARC iDT40 1PN 25A 30m A-SI | Acti9 Active | Acti9 Active
A9TYAE640 | ActI9 VigiARC iDT40 1PN 40A 30m A-SI | Acti9 Active | Acti9 Active
A9TYAE225 | Acti9 VigiARC iC60 2P 25A 30m A-SI | Acti9 Active | Acti9 Active
A9TYAE240 | Acti9 VigiARC iC60 2P 40A 30m A-SI | Acti9 Active | Acti9 Active
A9TYBE625 | Acti9 VigiARC iC40 1PN 25A 30m A-SI | Acti9 Active | Acti9 Active
A9TYBE640 | Acti9 VigiARC iC40 1PN 40A 30m A-SI | Acti9 Active | Acti9 Active
A9TYBE225 | Acti9 VigiARC iC60 2P 25A 30m A-SI | Acti9 Active | Acti9 Active
A9TYBE240 | Acti9 VigiARC iC60 2P 40A 30m A-SI | Acti9 Active | Acti9 Active
A9Y6E625 | Acti9 Vigi iDT40 1PN 25 A | Acti9 Active | Acti9 Active
A9Y6E640 | Acti9 Vigi iDT40 1PN 40 A | Acti9 Active | Acti9 Active
A9Y8E625 | Acti9 Vigi iC40 1PN 25 A | Acti9 Active | Acti9 Active
A9Y8E640 | Acti9 Vigi iC40 1PN 40 A | Acti9 Active | Acti9 Active
A9V6E225 | Acti9 Vigi iC60 2P 25 A | Acti9 Active | Acti9 Active
A9V6E240 | Acti9 Vigi iC60 2P 40 A | Acti9 Active | Acti9 Active
A9V8E225 | Acti9 Vigi iC60 2P 25 A | Acti9 Active | Acti9 Active
A9V8E240 | Acti9 Vigi iC60 2P 40 A | Acti9 Active | Acti9 Active
LV429453 | Wireless indication auxiliary for ComPacT NSXm and PowerPacT B-frame | Wireless indication auxiliary | Wireless indication auxiliary
LV429454 | Wireless indication auxiliary for ComPacT NSX, PowerPacT H-, J-, and L-Frame, ComPacT NS, and PowerPacT M-, P-frame | Wireless indication auxiliary | Wireless indication auxiliary
PD100X001 | PowerLogic PD100 Partial discharge monitoring solution | I/O module | Partial Discharge Box
A9XMC2D3 | PowerTag C 2DI 230V digital input module | I/O module | PowerTagC2DI
A9XMC1D3 | PowerTag C IO 230V digital input output module | I/O module | PowerTagCIO
LV933071 | MicroLogic Active 2.0 AP Control Unit for MasterPacT MTZ | Circuit breaker | MasterPacT MTZ Active AP
LV933072 | MicroLogic Active 5.0 AP Control Unit for MasterPacT MTZ | Circuit breaker | MasterPacT MTZ Active AP
LV933073 | MicroLogic Active 6.0 AP Control Unit for MasterPacT MTZ | Circuit breaker | MasterPacT MTZ Active AP
LV947600 | MicroLogic Active 2.0 EP Control Unit for MasterPacT MTZ | Circuit breaker | MasterPacT MTZ Active EP
LV947602 | MicroLogic Active 5.0 EP Control Unit for MasterPacT MTZ | Circuit breaker | MasterPacT MTZ Active EP
LV947603 | MicroLogic Active 6.0 EP Control Unit for MasterPacT MTZ | Circuit breaker | MasterPacT MTZ Active EP
OVA44210 | Exiway Light Act. connected 42/120 multi | Exiway Link | ExiwayLink
OVA44211 | Exiway Light Act. connected 65/120 multi | Exiway Link | ExiwayLink
OVA44212 | Exiway Light Act. connected 42/200 multi | Exiway Link | ExiwayLink
OVA44213 | Exiway Light Act. connected 65/200 multi | Exiway Link | ExiwayLink
OVA44214 | Exiway Light Act. connected 42/450 multi | Exiway Link | ExiwayLink
OVA44215 | Exiway Light Act. connected 65/450 multi | Exiway Link | ExiwayLink
OVA47210 | Exiway Trend Act. connected 42/120 multi | Exiway Link | ExiwayLink
OVA47211 | Exiway Trend Act. connected 65/120 multi | Exiway Link | ExiwayLink
OVA47212 | Exiway Trend Act. connected 42/200 multi | Exiway Link | ExiwayLink
OVA47213 | Exiway Trend Act. connected 65/200 multi | Exiway Link | ExiwayLink
OVA47214 | Exiway Trend Act. connected 42/450 multi | Exiway Link | ExiwayLink
OVA47215 | Exiway Trend Act. connected 65/450 multi | Exiway Link | ExiwayLink
OVA47222 | Exiway Light device | Exiway Link | ExiwayLink
OVA47223 | Exiway Light device | Exiway Link | ExiwayLink
OVA47224 | Exiway Light device | Exiway Link | ExiwayLink
OVA47225 | Exiway Light device | Exiway Link | ExiwayLink
OVA59130 | Exiway Light EVAC 42 SATI connected | Exiway Link | ExiwayLink
OVA59131 | Exiway Light EVAC 65 SATI connected | Exiway Link | ExiwayLink
OVA59230 | Exiway Light HAB 42 SATI connected | Exiway Link | ExiwayLink
OVA59231 | Exiway Light HAB 65 SATI connected | Exiway Link | ExiwayLink
OVA59330 | Exiway Light AMB 42 SATI connected | Exiway Link | ExiwayLink
OVA59331 | Exiway Light AMB 65 SATI connected | Exiway Link | ExiwayLink
OVA59430 | Exiway Light BIF 42 | Exiway Link | ExiwayLink
OVA59431 | Exiway Light BIF 65 | Exiway Link | ExiwayLink
OVA59232 | Exiway Light DBR 65 | Exiway Link | ExiwayLink
ZBRT1 | XB5R transmitter for wireless and batteryless pushbutton | I/O device | ZBRT
ZBRT2 | XB5R transmitter for wireless and batteryless pushbutton | I/O device | ZBRT

## Modbus Tables
Modbus Table Format and Data Types
EcoStruxure Panel Server System Modbus Registers
The EcoStruxure Panel Server assigns a Modbus address to each of the wireless devices paired with it. The Modbus address of the wireless devices is allocated automatically by the EcoStruxure Panel Server by selecting the first address available from address 100.
The Modbus address of a wireless device can be edited through the Panel Server webpages or with EcoStruxure Power Commission software with the parameters of the wireless device and updated with a value range from 1 to 247.
Note that starting with Panel Server firmware version 002.007.000, firmware update, commissioning, and configuration of Panel Server gateways by using EcoStruxure Power Commission software or Mobile app are no longer supported. For more information, refer to the related topic in DOCA0172•• EcoStruxure Panel Server - User Guide.
To read a value from a particular wireless device, the supervision system uses the Modbus address of the device.
The Panel Server implements its own Modbus registers (Panel Server tab) which start at address 255. Example: The firmware version of the Panel Server is available at address 255 + 121
The Panel Server delivers a synthesis table (Synthesis Table tab) which provides a consolidated view of information from all connected wireless devices at once. It is also possible to set values (write operation) for multiple devices at once. The Modbus address of the synthesis table can be configured through the Panel Server webpages (247 by default). See the Synthesis Table Format section below.
Go to Synthesis Table tab.
Modbus Register
The address of register number n is n-1. The tables detailed in the tabs of this file provide both register numbers (in decimal format) and corresponding addresses (in hexadecimal format) for the device that belongs to the device family indicated in the tab name of the table. To display the Modbus registers of your device in the correct device family tab, check the Commercial References tab that shows the commercial reference of the devices supported by the EcoStruxure Panel Server and the associated device family. Example: The Commercial References tab shows that PowerTag A9 M63 with commercial reference A9MEM1520 belongs to PowerTag Energy device family. The PowerTag Energy tab shows the Modbus registers available in A9MEM1520. Example of address: address of register number 3000 is 0x0BB7 (2999). NOTE: To know the description of the registers of each associated device (how to use them), print the PDF report of Modbus registers using EcoStruxure Power Commission software (refer to EcoStruxure Power Commission Online Help). This report gives a dynamic knowledge of all the registers potentially to be integrated into the supervision systems including a description of each register.
Table Format
Register tables have the following columns:
| Section | Address | Register | No. | RW | X | Unit | Type | Range | Invalid value | Saved | Function code | Description
| Designation |  | Description
| Section |  | Data category
| Address |  | 16-bit register address in hexadecimal. The address is the data used in the Modbus frame.
| Register |  | 16-bit register number in decimal. Register = Address + 1
| No |  | Number of 16-bit registers that need to be read/written to access the complete information
| R/RW |  | Whether the register is read only (R) or read-write (RW).
| X |  | Scale factor: • A scale of 1 means that the value of the register is the same as the value indicated. • A scale of 10 means that the register contains the value multiplied by 10. The actual value is therefore the value of the register divided by 10. • A scale of 0.1 means that the register contains the value multiplied by 0.1. The actual value is therefore the value of the register multiplied by 10.
| Unit |  | Information unit of measurement: • –: no unit corresponding to the value expressed. • h: hours • D: the unit depends on the connected device.
| Type |  | Coding data type (see Data type table below).
| Range |  | Range of permitted values for the variable, usually a subset of what the format allows. For BITMAP type data, the content of this domain is “–”.
| Invalid value |  | Invalid value for the variable
| Saved |  | Value saved when the power supply to the EcoStruxure Panel Server is switched off: • Y: the value of the register is saved. • N: the value is lost. NOTE: On start-up or reset, the available values are retrieved.
| Function code |  | Code of functions that can be used in the register.
| Description |  | Information about the register and the restrictions that apply.
Synthesis Table Format
The synthesis table provides a consolidated set of data from all the wireless devices in a single access. The table is organized into structured data blocks; each block contains the same data (for example, Product identifier) repeated for exactly 100 wireless devices (100 is the maximum number of wireless devices supported by Panel Server).
The synthesis table has the same columns than the register table (see the Table Format section above):
| Section | Address | Register | No. | RW | X | Unit | Type | Range | Invalid value | Saved | Function code | Description
The synthesis table also includes additional columns, one per device family (for example, CL110, ZBRT) to facilitate data retrieval.
| PTE63-PoTag QO | TH110 | CL110 | HeatTag | Acti9 Active | PowerTagC2DI | ... | ZBRT
| Designation |  | Description
| Device family (for example, CL110) |  | Use to filter registers applicable to the device family (for example, CL110). Navigate to the corresponding device family column and select "x" to retrieve the registers relevant to that device family.
| Description of data block |  | Each structured data block (for example, Communication status between Panel Server and wireless device) contains exactly 100 consecutive registers, corresponding to each of the 100 ranked wireless devices. The data block size remains fixed at 100 registers, regardless of the actual number of wireless devices discovered by the Panel Server. Each data block is organized as follows: Communication status between Panel Server and wireless device 1 Communication status between Panel Server and wireless device 2 .... Communication status between Panel Server and wireless device 100 For example, Register 40056 (dec) contains the Communication status between Panel Server and wireless device 28, where 28 is the rank of the wireless device (1-100).
Access to Modbus Registers from the Commercial Reference
Each supported wireless device is referenced in the Commercial References tab with: • Its commercial reference • Its device name • Its device family In the Commercial References tab, click the commercial reference of a device to automatically access the tab detailing its Modbus registers.
Filtering Data of Modbus Registers
In the tab of a device family, you can filter data of the registers using the filter function.
Data Types
| UINT16 |  | 16-bit unsigned integer (1 word) |  |  |  | 0 to 65535
| INT32 |  | 32-bit signed integer (2 words) |  |  |  | -2 147 483 648 to +2 147 483 647
| UINT32 |  | 32-bit unsigned integer (2 words) |  |  |  | 0 to 4 294 967 295
| INT64 |  | 64-bit signed integer (4 words) |  |  |  | -9 223 372 036 854 775 808 to 9 223 372 036 854 775 807 For Energy data, where the data type INT64 is indicated, the value limit is UINT48.
| UINT64 |  | 64-bit unsigned integer (4 words) |  |  |  | 0 to 18 446 744 073 709 600 000
| Float32 |  | 32-bit value (2 words) |  |  |  | -3.4028E+38 to +3.4028E+38
| ASCII |  | 8-bit alphanumeric character |  |  |  | Table of ASCII characters
| BITMAP |  | 16-bit field (1 word) |  |  |  | –
| DATETIME |  | Date and time in IEC 60870-5 format |  |  |  | See DATETIME below
Big-Endian Format
INT32, UINT32, INT64, and UINT64 variables are stored in big-endian format: the most significant register is transmitted first and the least significant register is transmitted at last place.
INT32, UINT32, INT64, and UINT64 variables are made of UINT16 variables.
The formulas to calculate the decimal value of these variables are: • INT32: (0-bit31)x231 + bit30x230 + bit29x229 + ...bit1x21 + bit0x20 • UINT32: bit31x231 + bit30x230 + bit29x229 + ...bit1x21 + bit0x20 • INT64: (0-bit63)x263 + bit62x262 + bit61x261 + ...bit1x21 + bit0x20 • UINT64: bit63x263 + bit62x262 + bit61x261 + ...bit1x21 + bit0x20
Example:
The total active energy delivered by a PowerTag Energy M250 M630 is an INT64 variable coded in registers 3208 to 3211.
If the values in the registers are: • register 3208 = 0 • register 3209 = 0 • register 3210 = 0x0017 or 23 • register 3211 = 0x9692 or 38546 as UINT16 variable and -26990 as INT16 variable (use the UINT16 value to calculate the value of the total active energy).
Then the total active energy is equal to 0x248 + 0x232 + 23x216 + 38546x20 = 1545874 Wh.
Data Type: Float32
Data type Float32 is represented in the single precision IEEE 754 (IEEE standard for floating-point arithmetic). A value N is calculated as indicated below:
N = (-1)S x 2E-127 x (1+M)
| Coefficient |  | Stands for |  | Description |  |  |  |  | Number of Bits
| S |  | Sign |  | Defines the sign of the value: 0 = positive 1 = negative |  |  |  |  | 1 bit
| E |  | Exponent |  | Excess 127 binary integer added. When 0 < E < 255, the actual exponent is: e = E - 127. |  |  |  |  | 8 bits
| M |  | Mantissa |  | Magnitude, normalized binary significant |  |  |  |  | 23 bits
Example:
0 = 0 00000000 00000000000000000000000 -1.5 = 1 01111111 10000000000000000000000 with: • S = 1 • E = 01111111 = 127 • M = 10000000000000000000000 = 1x2-1 + 0x2-2 +...+ 0x2-23 = 0.5 • N = (-1) x 20 x (1+0.5) = -1.5
Data Type: DATETIME
DATETIME is a data type used to code date and time defined by IEC 60870-5 standard.
| Register | Type | Bit | Range |  | Description
| 1 | UINT16 | 0–6 | 0x00–0x7F |  | Year:
0x00 (00) to 0x7F (127) correspond to years 2000 to 2127.
For example, 0x0D (13) corresponds to year 2013.
|  |  | 7–15 | – |  | Reserved
| 2 | UINT16 | 0–4 | 0x01–0x1F |  | Day
|  |  | 5–7 | – |  | Reserved
|  |  | 8–11 | 0x00–0x0C |  | Month
|  |  | 12–15 | – |  | Reserved
| 3 | UINT16 | 0–5 | 0x00–0x3B |  | Minutes
|  |  | 6–7 | – |  | Reserved
|  |  | 8–12 | 0x00–0x17 |  | Hours
|  |  | 13–15 | – |  | Reserved
| 4 | UINT16 | 0–15 | 0x0000–0xEA5F |  | Milliseconds
Example of Modbus Frames
Request
| Definition |  | Number of Bytes |  | Value | Comment
| Server number |  | 1 byte |  | 0x05 | EcoStruxure Panel Server Modbus Address
| Function code |  | 1 byte |  | 0x03 | Reads n output or internal words
| Address |  | 2 bytes |  | 0x36E2 | Address of a consumption meter whose address is 14050 in decimal notation.
| Number of words |  | 2 bytes |  | 0x002C | Reads 44 16-bit registers.
| CRC |  | 2 bytes |  | xxxx | Value of CRC16
Response
| Definition |  | Number of Bytes |  | Value | Comment
| Server number |  | 1 byte |  | 0x05 | EcoStruxure Panel Server Modbus Address
| Function code |  | 1 byte |  | 0x03 | Reads n output or internal words
| Number of Bytes |  | 2 bytes |  | 0x0058 | Number of bytes read
| Number of words read |  | 88 bytes |  | – | Reads 44 16-bit registers.
| CRC |  | 2 bytes |  | xxxx | Value of CRC16

## Legal Information
Legal Information
The information provided in this document contains general descriptions, technical characteristics and/or recommendations related to products/solutions. This document is not intended as a substitute for a detailed study or operational and site-specific development or schematic plan. It is not to be used for determining suitability or reliability of the products/solutions for specific user applications. It is the duty of any such user to perform or have any professional expert of its choice (integrator, specifier or the like) perform the appropriate and comprehensive risk analysis, evaluation and testing of the products/solutions with respect to the relevant specific application or use thereof. The Schneider Electric brand and any trademarks of Schneider Electric and its subsidiaries referred to in this document are the property of Schneider Electric SE or its subsidiaries. All other brands may be trademarks of their respective owner. This document and its content are protected under applicable copyright laws and provided for informative use only. No part of this document may be reproduced or transmitted in any form or by any means (electronic, mechanical, photocopying, recording, or otherwise), for any purpose, without the prior written permission of Schneider Electric. Schneider Electric does not grant any right or license for commercial use of the document or its content, except for a non-exclusive and personal license to consult it on an "as is" basis. Electrical equipment should be installed, operated, serviced, and maintained only by qualified personnel. No responsibility is assumed by Schneider Electric for any consequences arising out of the use of this material. Schneider Electric reserves the right to make changes or updates with respect to or in the content of this document or the format thereof, at any time without notice. To the extent permitted by applicable law, no responsibility or liability is assumed by Schneider Electric and its subsidiaries for any errors or omissions in the informational content of this document, as well as any non-intended use or misuse of the content thereof.

## Panel Server
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Identification | 0x000A | 11 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Product range
Identification | 0x001A | 27 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Product family
Identification | 0x002A | 43 | 17 | R | - | - | ASCII |  | 0x00000000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Vendor URL
Identification | 0x003C | 61 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial Reference - Example "PAS600L"
Identification | 0x0050 | 81 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | EcoStruxure Panel Server hardware version on 11 ASCII characters, valid for firmware version 001.008.007 and later. Example: 000.000.001
Identification | 0x0064 | 101 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Serial number on 12 ASCII characters; 12 alphanumeric digits maximum [SN] or [S/N]: PP YY WW [D L[nnnn]] • PP: Plant • YY: Year in decimal notation [05...99] • WW: Week in decimal notation [1...53] • D: Day of the week in decimal notation [1...7] • L: Line or machine number or team [1...9] • nnnn: Sequence of numbers [0001...10.000–1]
Date and Time | 0x0073 | 116 | 4 | RW | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4, 16 | Indicates the year, month, day, hour, minute and millisecond on EcoStruxure Panel Server. Refer to DATETIME.
Identification | 0x0078 | 121 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | EcoStruxure Panel Server firmware version on 11 ASCII characters, valid for firmware version 001.008.007 and later. Example: 001.008.007
Identification | 0x007E | 127 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Product capability
Identification | 0x008E | 143 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Additionnal product capability
Health State | 0x009E | 159 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Health state of EcoStruxure Panel Server • 0 = Nominal • 1 = Degraded • 2 = Out of order
Identification | 0x009F | 160 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Manufacturer Name - "Schneider Electric"
Synthesis Table Server adress | 0x00FA | 251 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Synthesis Table server address (Default @247)
List of wireless devices | 0x01F4 | 501 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 1
List of wireless devices | 0x01F8 | 505 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 1
List of wireless devices | 0x01F9 | 506 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 2
List of wireless devices | 0x01FD | 510 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 2
List of wireless devices | 0x01FE | 511 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 3
List of wireless devices | 0x0202 | 515 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 3
List of wireless devices | 0x0203 | 516 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 4
List of wireless devices | 0x0207 | 520 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 4
List of wireless devices | 0x0208 | 521 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 5
List of wireless devices | 0x020C | 525 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 5
List of wireless devices | 0x020D | 526 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 6
List of wireless devices | 0x0211 | 530 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 6
List of wireless devices | 0x0212 | 531 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 7
List of wireless devices | 0x0216 | 535 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 7
List of wireless devices | 0x0217 | 536 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 8
List of wireless devices | 0x021B | 540 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 8
List of wireless devices | 0x021C | 541 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 9
List of wireless devices | 0x0220 | 545 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 9
List of wireless devices | 0x0221 | 546 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 10
List of wireless devices | 0x0225 | 550 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 10
List of wireless devices | 0x0226 | 551 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 11
List of wireless devices | 0x022A | 555 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 11
List of wireless devices | 0x022B | 556 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 12
List of wireless devices | 0x022F | 560 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 12
List of wireless devices | 0x0230 | 561 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 13
List of wireless devices | 0x0234 | 565 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 13
List of wireless devices | 0x0235 | 566 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 14
List of wireless devices | 0x0239 | 570 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 14
List of wireless devices | 0x023A | 571 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 15
List of wireless devices | 0x023E | 575 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 15
List of wireless devices | 0x023F | 576 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 16
List of wireless devices | 0x0243 | 580 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 16
List of wireless devices | 0x0244 | 581 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 17
List of wireless devices | 0x0248 | 585 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 17
List of wireless devices | 0x0249 | 586 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 18
List of wireless devices | 0x024D | 590 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 18
List of wireless devices | 0x024E | 591 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 19
List of wireless devices | 0x0252 | 595 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 19
List of wireless devices | 0x0253 | 596 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 20
List of wireless devices | 0x0257 | 600 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 20
List of wireless devices | 0x0258 | 601 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 21
List of wireless devices | 0x025C | 605 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 21
List of wireless devices | 0x025D | 606 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 22
List of wireless devices | 0x0261 | 610 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 22
List of wireless devices | 0x0262 | 611 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 23
List of wireless devices | 0x0266 | 615 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 23
List of wireless devices | 0x0267 | 616 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 24
List of wireless devices | 0x026B | 620 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 24
List of wireless devices | 0x026C | 621 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 25
List of wireless devices | 0x0270 | 625 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 25
List of wireless devices | 0x0271 | 626 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 26
List of wireless devices | 0x0275 | 630 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 26
List of wireless devices | 0x0276 | 631 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 27
List of wireless devices | 0x027A | 635 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 27
List of wireless devices | 0x027B | 636 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 28
List of wireless devices | 0x027F | 640 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 28
List of wireless devices | 0x0280 | 641 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 29
List of wireless devices | 0x0284 | 645 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 29
List of wireless devices | 0x0285 | 646 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 30
List of wireless devices | 0x0289 | 650 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 30
List of wireless devices | 0x028A | 651 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 31
List of wireless devices | 0x028E | 655 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 31
List of wireless devices | 0x028F | 656 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 32
List of wireless devices | 0x0293 | 660 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 32
List of wireless devices | 0x0294 | 661 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 33
List of wireless devices | 0x0298 | 665 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 33
List of wireless devices | 0x0299 | 666 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 34
List of wireless devices | 0x029D | 670 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 34
List of wireless devices | 0x029E | 671 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 35
List of wireless devices | 0x02A2 | 675 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 35
List of wireless devices | 0x02A3 | 676 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 36
List of wireless devices | 0x02A7 | 680 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 36
List of wireless devices | 0x02A8 | 681 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 37
List of wireless devices | 0x02AC | 685 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 37
List of wireless devices | 0x02AD | 686 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 38
List of wireless devices | 0x02B1 | 690 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 38
List of wireless devices | 0x02B2 | 691 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 39
List of wireless devices | 0x02B6 | 695 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 39
List of wireless devices | 0x02B7 | 696 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 40
List of wireless devices | 0x02BB | 700 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 40
List of wireless devices | 0x02BC | 701 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 41
List of wireless devices | 0x02C0 | 705 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 41
List of wireless devices | 0x02C1 | 706 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 42
List of wireless devices | 0x02C5 | 710 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 42
List of wireless devices | 0x02C6 | 711 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 43
List of wireless devices | 0x02CA | 715 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 43
List of wireless devices | 0x02CB | 716 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 44
List of wireless devices | 0x02CF | 720 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 44
List of wireless devices | 0x02D0 | 721 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 45
List of wireless devices | 0x02D4 | 725 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 45
List of wireless devices | 0x02D5 | 726 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 46
List of wireless devices | 0x02D9 | 730 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 46
List of wireless devices | 0x02DA | 731 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 47
List of wireless devices | 0x02DE | 735 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 47
List of wireless devices | 0x02DF | 736 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 48
List of wireless devices | 0x02E3 | 740 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 48
List of wireless devices | 0x02E4 | 741 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 49
List of wireless devices | 0x02E8 | 745 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 49
List of wireless devices | 0x02E9 | 746 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 50
List of wireless devices | 0x02ED | 750 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 50
List of wireless devices | 0x02EE | 751 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 51
List of wireless devices | 0x02F2 | 755 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 51
List of wireless devices | 0x02F3 | 756 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 52
List of wireless devices | 0x02F7 | 760 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 52
List of wireless devices | 0x02F8 | 761 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 53
List of wireless devices | 0x02FC | 765 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 53
List of wireless devices | 0x02FD | 766 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 54
List of wireless devices | 0x0301 | 770 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 54
List of wireless devices | 0x0302 | 771 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 55
List of wireless devices | 0x0306 | 775 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 55
List of wireless devices | 0x0307 | 776 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 56
List of wireless devices | 0x030B | 780 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 56
List of wireless devices | 0x030C | 781 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 57
List of wireless devices | 0x0310 | 785 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 57
List of wireless devices | 0x0311 | 786 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 58
List of wireless devices | 0x0315 | 790 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 58
List of wireless devices | 0x0316 | 791 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 59
List of wireless devices | 0x031A | 795 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 59
List of wireless devices | 0x031B | 796 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 60
List of wireless devices | 0x031F | 800 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 60
List of wireless devices | 0x0320 | 801 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 61
List of wireless devices | 0x0324 | 805 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 61
List of wireless devices | 0x0325 | 806 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 62
List of wireless devices | 0x0329 | 810 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 62
List of wireless devices | 0x032A | 811 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 63
List of wireless devices | 0x032E | 815 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 63
List of wireless devices | 0x032F | 816 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 64
List of wireless devices | 0x0333 | 820 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 64
List of wireless devices | 0x0334 | 821 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 65
List of wireless devices | 0x0338 | 825 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 65
List of wireless devices | 0x0339 | 826 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 66
List of wireless devices | 0x033D | 830 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 66
List of wireless devices | 0x033E | 831 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 67
List of wireless devices | 0x0342 | 835 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 67
List of wireless devices | 0x0343 | 836 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 68
List of wireless devices | 0x0347 | 840 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 68
List of wireless devices | 0x0348 | 841 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 69
List of wireless devices | 0x034C | 845 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 69
List of wireless devices | 0x034D | 846 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 70
List of wireless devices | 0x0351 | 850 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 70
List of wireless devices | 0x0352 | 851 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 71
List of wireless devices | 0x0356 | 855 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 71
List of wireless devices | 0x0357 | 856 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 72
List of wireless devices | 0x035B | 860 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 72
List of wireless devices | 0x035C | 861 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 73
List of wireless devices | 0x0360 | 865 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 73
List of wireless devices | 0x0361 | 866 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 74
List of wireless devices | 0x0365 | 870 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 74
List of wireless devices | 0x0366 | 871 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 75
List of wireless devices | 0x036A | 875 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 75
List of wireless devices | 0x036B | 876 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 76
List of wireless devices | 0x036F | 880 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 76
List of wireless devices | 0x0370 | 881 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 77
List of wireless devices | 0x0374 | 885 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 77
List of wireless devices | 0x0375 | 886 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 78
List of wireless devices | 0x0379 | 890 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 78
List of wireless devices | 0x037A | 891 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 79
List of wireless devices | 0x037E | 895 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 79
List of wireless devices | 0x037F | 896 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 80
List of wireless devices | 0x0383 | 900 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 80
List of wireless devices | 0x0384 | 901 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 81
List of wireless devices | 0x0388 | 905 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 81
List of wireless devices | 0x0389 | 906 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 82
List of wireless devices | 0x038D | 910 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 82
List of wireless devices | 0x038E | 911 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 83
List of wireless devices | 0x0392 | 915 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 83
List of wireless devices | 0x0393 | 916 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 84
List of wireless devices | 0x0397 | 920 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 84
List of wireless devices | 0x0398 | 921 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 85
List of wireless devices | 0x039C | 925 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 85
List of wireless devices | 0x039D | 926 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 86
List of wireless devices | 0x03A1 | 930 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 86
List of wireless devices | 0x03A2 | 931 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 87
List of wireless devices | 0x03A6 | 935 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 87
List of wireless devices | 0x03A7 | 936 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 88
List of wireless devices | 0x03AB | 940 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 88
List of wireless devices | 0x03AC | 941 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 89
List of wireless devices | 0x03B0 | 945 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 89
List of wireless devices | 0x03B1 | 946 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 90
List of wireless devices | 0x03B5 | 950 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 90
List of wireless devices | 0x03B6 | 951 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 91
List of wireless devices | 0x03BA | 955 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 91
List of wireless devices | 0x03BB | 956 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 92
List of wireless devices | 0x03BF | 960 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 92
List of wireless devices | 0x03C0 | 961 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 93
List of wireless devices | 0x03C4 | 965 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 93
List of wireless devices | 0x03C5 | 966 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 94
List of wireless devices | 0x03C9 | 970 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 94
List of wireless devices | 0x03CA | 971 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 95
List of wireless devices | 0x03CE | 975 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 95
List of wireless devices | 0x03CF | 976 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 96
List of wireless devices | 0x03D3 | 980 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 96
List of wireless devices | 0x03D4 | 981 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 97
List of wireless devices | 0x03D8 | 985 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 97
List of wireless devices | 0x03D9 | 986 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 98
List of wireless devices | 0x03DD | 990 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 98
List of wireless devices | 0x03DE | 991 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 99
List of wireless devices | 0x03E2 | 995 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 99
List of wireless devices | 0x03E3 | 996 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 100
List of wireless devices | 0x03E7 | 1000 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 100
Local Digital Inputs | 0x03E8 | 1001 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | DI1 validity. If a device is connected on DI1, a valid value is returned (= 1). Otherwise an invalid value is returned.
Local Digital Inputs | 0x03E9 | 1002 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | DI2 validity. If a device is connected on DI2, a valid value is returned (= 1). Otherwise an invalid value is returned.
Local Digital Inputs | 0x03EA | 1003 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | DI1 input mode • 0 = Pulse • 1 = Status
Local Digital Inputs | 0x03EB | 1004 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | DI2 input mode • 0 = Pulse • 1 = Status
Local Digital Inputs | 0x03EC | 1005 | 20 | R | - | - | ASCII |  | 0x00000000000000000000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | User application name of the device connected on DI1
Local Digital Inputs | 0x0400 | 1025 | 20 | R | - | - | ASCII |  | 0x00000000000000000000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | User application name of the device connected on DI2
Local Digital Inputs | 0x0414 | 1045 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Electrical label of the device connected on DI1
Local Digital Inputs | 0x0417 | 1048 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Electrical label of the device connected on DI2
Local Digital Inputs | 0x041A | 1051 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the usage of the device connected on DI1 • 1 = Main/Incomer • 2 = Sub/Head of group • 3 = Heating • 4 = Cooling • 5 = HVAC • 6 = Ventilation • 7 = Lighting • 8 = Office Equipment • 9 = Cooking • 10 = Food refrigeration • 11 = Elevators • 12 = Computers • 13 = Renewable power source • 14 = Genset • 15 = Compressed air • 16 = Vapor • 17 = Machine • 18 = Process • 19 = Water • 20 = Other Sockets • 21 = Other • 22 = Electrical vehicle charging station • 23 = Loads associated with renewable power source • 24 = Plug loads • 25 = Air conditionning • 26 = Domestic hot water • 27 = Heating and air conditionning • 28 = Hot sanitary water • 29 = IT • 30 = Lighting (interior) • 31 = Lighting (exterior and park) • 32 = Mixed usages • 33 = Refrigeration • 34 = Special loads • 35 = Total • 36 = Transportation system • 37 = Water system pumps • 38 = Emergency lighting
Local Digital Inputs | 0x041B | 1052 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the usage of the device connected on DI2 • 1 = Main/Incomer • 2 = Sub/Head of group • 3 = Heating • 4 = Cooling • 5 = HVAC • 6 = Ventilation • 7 = Lighting • 8 = Office Equipment • 9 = Cooking • 10 = Food refrigeration • 11 = Elevators • 12 = Computers • 13 = Renewable power source • 14 = Genset • 15 = Compressed air • 16 = Vapor • 17 = Machine • 18 = Process • 19 = Water • 20 = Other Sockets • 21 = Other • 22 = Electrical vehicle charging station • 23 = Loads associated with renewable power source • 24 = Plug loads • 25 = Air conditionning • 26 = Domestic hot water • 27 = Heating and air conditionning • 28 = Hot sanitary water • 29 = IT • 30 = Lighting (interior) • 31 = Lighting (exterior and park) • 32 = Mixed usages • 33 = Refrigeration • 34 = Special loads • 35 = Total • 36 = Transportation system • 37 = Water system pumps • 38 = Emergency lighting
Local Digital Inputs | 0x041C | 1053 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Logical status of the Digital Input DI1 (takes into account the configured polarity) ON // Active OFF // Inactive Undetermined // Invalid value
Local Digital Inputs | 0x041D | 1054 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Logical status of the Digital Input DI2 (takes into account the configured polarity) ON // Active OFF // Inactive Undetermined // Invalid value
Local Digital Inputs | 0x041E | 1055 | 2 | R | - | - | UINT32 |  | 0xFFFFFFFF | Y | 3, 100-4 | Non resettable DI1 operating time
Local Digital Inputs | 0x0420 | 1057 | 2 | R | - | - | UINT32 |  | 0xFFFFFFFF | Y | 3, 100-4 | Non resettable DI2 operating time
Local Digital Inputs | 0x0422 | 1059 | 2 | RW | - | - | UINT32 |  | 0xFFFFFFFF | Y | 3, 100-4, 16 | Resettable DI1 operating time
Local Digital Inputs | 0x0424 | 1061 | 2 | RW | - | - | UINT32 |  | 0xFFFFFFFF | Y | 3, 100-4, 16 | Resettable DI2 operating time
Local Digital Inputs | 0x0426 | 1063 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | DI1 last reset operating time date
Local Digital Inputs | 0x042A | 1067 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | DI2 last reset operating time date
Local Digital Inputs | 0x042E | 1071 | 2 | R | - | - | UINT32 |  | 0xFFFFFFFF | Y | 3, 100-4 | Non resettable DI1 operation counter
Local Digital Inputs | 0x0430 | 1073 | 2 | R | - | - | UINT32 |  | 0xFFFFFFFF | Y | 3, 100-4 | Non resettable DI2 operation counter
Local Digital Inputs | 0x0432 | 1075 | 2 | RW | - | - | UINT32 |  | 0xFFFFFFFF | Y | 3, 100-4, 16 | Resettable DI1 operation counter
Local Digital Inputs | 0x0434 | 1077 | 2 | RW | - | - | UINT32 |  | 0xFFFFFFFF | Y | 3, 100-4, 16 | Resettable DI2 operation counter
Local Digital Inputs | 0x0436 | 1079 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | DI1 last reset operation counter date
Local Digital Inputs | 0x043A | 1083 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | DI2 last reset operation counter date
Local Digital Inputs | 0x043E | 1087 | 2 | R | - | - | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Pulse weight of device connected on DI1 if DI1 mode is set to Pulse
Local Digital Inputs | 0x0440 | 1089 | 2 | R | - | - | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Pulse weight of device connected on DI2 if DI2 mode is set to Pulse
Local Digital Inputs | 0x0442 | 1091 | 4 | R | - | - | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Offset applied on DI1 is DI1 mode if set to Pulse
Local Digital Inputs | 0x0446 | 1095 | 4 | R | - | - | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Offset applied on DI2 is DI2 mode if set to Pulse
Local Digital Inputs | 0x044A | 1099 | 4 | R | - | - | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Non-resettable pulse counter on DI1 if DI1 mode is set to Pulse
Local Digital Inputs | 0x044E | 1103 | 4 | R | - | - | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Non-resettable pulse counter on DI2 if DI2 mode is set to Pulse
Local Digital Inputs | 0x0452 | 1107 | 4 | RW | - | - | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Resettable DI1 pulse count
Local Digital Inputs | 0x0456 | 1111 | 4 | RW | - | - | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Resettable DI2 pulse count
Local Digital Inputs | 0x045A | 1115 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Date of last reset pulse counter for DI1
Local Digital Inputs | 0x045E | 1119 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Date of last reset pulse counter for DI2
Local Digital Inputs | 0x0462 | 1123 | 4 | R | - | - | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Metering accumulated value on DI1 if DI1 mode is set to Pulse. The unit of the metering accumulated value depends on the DI1 configuration 0 None (None/empty) None/empty (None/empty) 1 ElectricalMeasurement.Delivered+ReceivedActiveEnergyPhsA (Wh) ElectricalMeasurement.RmsActivePowerPhsA (W) 2 ElectricalMeasurement.Delivered-ReceivedActiveEnergyPhsA (Wh) ElectricalMeasurement.RmsActivePowerPhsA (W) 3 ElectricalMeasurement.DeliveredActiveEnergyPhsA (Wh) ElectricalMeasurement.RmsActivePowerPhsA (W) 4 ElectricalMeasurement.ReceivedActiveEnergyPhsA (Wh) ElectricalMeasurement.RmsActivePowerPhsA (W) 5 ElectricalMeasurement.Delivered+ReceivedActiveEnergyPhsB (Wh) ElectricalMeasurement.RmsActivePowerPhsB (W) 6 ElectricalMeasurement.Delivered-ReceivedActiveEnergyPhsB (Wh) ElectricalMeasurement.RmsActivePowerPhsB (W) 7 ElectricalMeasurement.DeliveredActiveEnergyPhsB (Wh) ElectricalMeasurement.RmsActivePowerPhsB (W) 8 ElectricalMeasurement.ReceivedActiveEnergyPhsB (Wh) ElectricalMeasurement.RmsActivePowerPhsB (W) 9 ElectricalMeasurement.Delivered+ReceivedActiveEnergyPhsC (Wh) ElectricalMeasurement.RmsActivePowerPhsC (W) 10 ElectricalMeasurement.Delivered-ReceivedActiveEnergyPhsC (Wh) ElectricalMeasurement.RmsActivePowerPhsC (W) 11 ElectricalMeasurement.DeliveredActiveEnergyPhsC (Wh) ElectricalMeasurement.RmsActivePowerPhsC (W) 12 ElectricalMeasurement.ReceivedActiveEnergyPhsC (Wh) ElectricalMeasurement.RmsActivePowerPhsC (W) 13 ElectricalMeasurement.TotalDelivered+ReceivedActiveEnergy (Wh) ElectricalMeasurement.TotalRmsActivePower (W) 14 ElectricalMeasurement.TotalDelivered-ReceivedActiveEnergy (Wh) ElectricalMeasurement.TotalRmsActivePower (W) 15 ElectricalMeasurement.TotalDeliveredActiveEnergy (Wh) ElectricalMeasurement.TotalRmsActivePower (W) 16 ElectricalMeasurement.TotalReceivedActiveEnergy (Wh) ElectricalMeasurement.TotalRmsActivePower (W) 17 ElectricalMeasurement.Delivered+ReceivedReactiveEnergyPhsA (Varh) ElectricalMeasurement.RmsReactivePowerPhsA (Var) 18 ElectricalMeasurement.Delivered-ReceivedReactiveEnergyPhsA (Varh) ElectricalMeasurement.RmsReactivePowerPhsA (Var) 19 ElectricalMeasurement.DeliveredReactiveEnergyPhsA (Varh) ElectricalMeasurement.RmsReactivePowerPhsA (Var) 20 ElectricalMeasurement.ReceivedReactiveEnergyPhsA (Varh) ElectricalMeasurement.RmsReactivePowerPhsA (Var) 21 ElectricalMeasurement.Delivered+ReceivedReactiveEnergyPhsB (Varh) ElectricalMeasurement.RmsReactivePowerPhsB (Var) 22 ElectricalMeasurement.Delivered-ReceivedReactiveEnergyPhsB (Varh) ElectricalMeasurement.RmsReactivePowerPhsB (Var) 23 ElectricalMeasurement.DeliveredReactiveEnergyPhsB (Varh) ElectricalMeasurement.RmsReactivePowerPhsB (Var) 24 ElectricalMeasurement.ReceivedReactiveEnergyPhsB (Varh) ElectricalMeasurement.RmsReactivePowerPhsB (Var) 25 ElectricalMeasurement.Delivered+ReceivedReactiveEnergyPhsC (Varh) ElectricalMeasurement.RmsReactivePowerPhsC (Var) 26 ElectricalMeasurement.Delivered-ReceivedReactiveEnergyPhsC (Varh) ElectricalMeasurement.RmsReactivePowerPhsC (Var) 27 ElectricalMeasurement.DeliveredReactiveEnergyPhsC (Varh) ElectricalMeasurement.RmsReactivePowerPhsC (Var) 28 ElectricalMeasurement.ReceivedReactiveEnergyPhsC (Varh) ElectricalMeasurement.RmsReactivePowerPhsC (Var) 29 ElectricalMeasurement.TotalDelivered+ReceivedReactiveEnergy (Varh) ElectricalMeasurement.TotalRmsReactivePower (Var) 30 ElectricalMeasurement.TotalDelivered-ReceivedReactiveEnergy (Varh) ElectricalMeasurement.TotalRmsReactivePower (Var) 31 ElectricalMeasurement.TotalDeliveredReactiveEnergy (Varh) ElectricalMeasurement.TotalRmsReactivePower (Var) 32 ElectricalMeasurement.TotalReceivedReactiveEnergy (Varh) ElectricalMeasurement.TotalRmsReactivePower (Var) 33 ElectricalMeasurement.Delivered+ReceivedApparentEnergyPhsA (VAh) ElectricalMeasurement.RmsApparentPowerPhsA (VA) 34 ElectricalMeasurement.Delivered-ReceivedApparentEnergyPhsA (VAh) ElectricalMeasurement.RmsApparentPowerPhsA (VA) 35 ElectricalMeasurement.DeliveredApparentEnergyPhsA (VAh) ElectricalMeasurement.RmsApparentPowerPhsA (VA) 36 ElectricalMeasurement.ReceivedApparentEnergyPhsA (VAh) ElectricalMeasurement.RmsApparentPowerPhsA (VA) 37 ElectricalMeasurement.Delivered+ReceivedApparentEnergyPhsB (VAh) ElectricalMeasurement.RmsApparentPowerPhsB (VA) 38 ElectricalMeasurement.Delivered-ReceivedApparentEnergyPhsB (VAh) ElectricalMeasurement.RmsApparentPowerPhsB (VA) 39 ElectricalMeasurement.DeliveredApparentEnergyPhsB (VAh) ElectricalMeasurement.RmsApparentPowerPhsB (VA) 40 ElectricalMeasurement.ReceivedApparentEnergyPhsB (VAh) ElectricalMeasurement.RmsApparentPowerPhsB (VA) 41 ElectricalMeasurement.Delivered+ReceivedApparentEnergyPhsC (VAh) ElectricalMeasurement.RmsApparentPowerPhsC (VA) 42 ElectricalMeasurement.Delivered-ReceivedApparentEnergyPhsC (VAh) ElectricalMeasurement.RmsApparentPowerPhsC (VA) 43 ElectricalMeasurement.DeliveredApparentEnergyPhsC (VAh) ElectricalMeasurement.RmsApparentPowerPhsC (VA) 44 ElectricalMeasurement.ReceivedApparentEnergyPhsC (VAh) ElectricalMeasurement.RmsApparentPowerPhsC (VA) 45 ElectricalMeasurement.TotalDelivered+ReceivedApparentEnergy (VAh) ElectricalMeasurement.TotalRmsApparentPower (VA) 46 ElectricalMeasurement.TotalDelivered-ReceivedApparentEnergy (VAh) ElectricalMeasurement.TotalRmsApparentPower (VA) 47 ElectricalMeasurement.TotalDeliveredApparentEnergy (VAh) ElectricalMeasurement.TotalRmsApparentPower (VA) 48 ElectricalMeasurement.TotalReceivedApparentEnergy (VAh) ElectricalMeasurement.TotalRmsApparentPower (VA) 49 WaterVolume (m³) WaterFlowRate ( m³/h) 50 GasVolume (m³) GasFlowRate ( m³/h) 51 HeatEnergy (Wh) HeatPower (W) 52 ChilledEnergy (Wh) ChilledPower (W) 53 Custom Custom
Local Digital Inputs | 0x0466 | 1127 | 4 | R | - | - | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Metering accumulated value on DI2 if DI2 mode is set to Pulse. The unit of the metering accumulated value depends on the DI2 configuration 0 None (None/empty) None/empty (None/empty) 1 ElectricalMeasurement.Delivered+ReceivedActiveEnergyPhsA (Wh) ElectricalMeasurement.RmsActivePowerPhsA (W) 2 ElectricalMeasurement.Delivered-ReceivedActiveEnergyPhsA (Wh) ElectricalMeasurement.RmsActivePowerPhsA (W) 3 ElectricalMeasurement.DeliveredActiveEnergyPhsA (Wh) ElectricalMeasurement.RmsActivePowerPhsA (W) 4 ElectricalMeasurement.ReceivedActiveEnergyPhsA (Wh) ElectricalMeasurement.RmsActivePowerPhsA (W) 5 ElectricalMeasurement.Delivered+ReceivedActiveEnergyPhsB (Wh) ElectricalMeasurement.RmsActivePowerPhsB (W) 6 ElectricalMeasurement.Delivered-ReceivedActiveEnergyPhsB (Wh) ElectricalMeasurement.RmsActivePowerPhsB (W) 7 ElectricalMeasurement.DeliveredActiveEnergyPhsB (Wh) ElectricalMeasurement.RmsActivePowerPhsB (W) 8 ElectricalMeasurement.ReceivedActiveEnergyPhsB (Wh) ElectricalMeasurement.RmsActivePowerPhsB (W) 9 ElectricalMeasurement.Delivered+ReceivedActiveEnergyPhsC (Wh) ElectricalMeasurement.RmsActivePowerPhsC (W) 10 ElectricalMeasurement.Delivered-ReceivedActiveEnergyPhsC (Wh) ElectricalMeasurement.RmsActivePowerPhsC (W) 11 ElectricalMeasurement.DeliveredActiveEnergyPhsC (Wh) ElectricalMeasurement.RmsActivePowerPhsC (W) 12 ElectricalMeasurement.ReceivedActiveEnergyPhsC (Wh) ElectricalMeasurement.RmsActivePowerPhsC (W) 13 ElectricalMeasurement.TotalDelivered+ReceivedActiveEnergy (Wh) ElectricalMeasurement.TotalRmsActivePower (W) 14 ElectricalMeasurement.TotalDelivered-ReceivedActiveEnergy (Wh) ElectricalMeasurement.TotalRmsActivePower (W) 15 ElectricalMeasurement.TotalDeliveredActiveEnergy (Wh) ElectricalMeasurement.TotalRmsActivePower (W) 16 ElectricalMeasurement.TotalReceivedActiveEnergy (Wh) ElectricalMeasurement.TotalRmsActivePower (W) 17 ElectricalMeasurement.Delivered+ReceivedReactiveEnergyPhsA (Varh) ElectricalMeasurement.RmsReactivePowerPhsA (Var) 18 ElectricalMeasurement.Delivered-ReceivedReactiveEnergyPhsA (Varh) ElectricalMeasurement.RmsReactivePowerPhsA (Var) 19 ElectricalMeasurement.DeliveredReactiveEnergyPhsA (Varh) ElectricalMeasurement.RmsReactivePowerPhsA (Var) 20 ElectricalMeasurement.ReceivedReactiveEnergyPhsA (Varh) ElectricalMeasurement.RmsReactivePowerPhsA (Var) 21 ElectricalMeasurement.Delivered+ReceivedReactiveEnergyPhsB (Varh) ElectricalMeasurement.RmsReactivePowerPhsB (Var) 22 ElectricalMeasurement.Delivered-ReceivedReactiveEnergyPhsB (Varh) ElectricalMeasurement.RmsReactivePowerPhsB (Var) 23 ElectricalMeasurement.DeliveredReactiveEnergyPhsB (Varh) ElectricalMeasurement.RmsReactivePowerPhsB (Var) 24 ElectricalMeasurement.ReceivedReactiveEnergyPhsB (Varh) ElectricalMeasurement.RmsReactivePowerPhsB (Var) 25 ElectricalMeasurement.Delivered+ReceivedReactiveEnergyPhsC (Varh) ElectricalMeasurement.RmsReactivePowerPhsC (Var) 26 ElectricalMeasurement.Delivered-ReceivedReactiveEnergyPhsC (Varh) ElectricalMeasurement.RmsReactivePowerPhsC (Var) 27 ElectricalMeasurement.DeliveredReactiveEnergyPhsC (Varh) ElectricalMeasurement.RmsReactivePowerPhsC (Var) 28 ElectricalMeasurement.ReceivedReactiveEnergyPhsC (Varh) ElectricalMeasurement.RmsReactivePowerPhsC (Var) 29 ElectricalMeasurement.TotalDelivered+ReceivedReactiveEnergy (Varh) ElectricalMeasurement.TotalRmsReactivePower (Var) 30 ElectricalMeasurement.TotalDelivered-ReceivedReactiveEnergy (Varh) ElectricalMeasurement.TotalRmsReactivePower (Var) 31 ElectricalMeasurement.TotalDeliveredReactiveEnergy (Varh) ElectricalMeasurement.TotalRmsReactivePower (Var) 32 ElectricalMeasurement.TotalReceivedReactiveEnergy (Varh) ElectricalMeasurement.TotalRmsReactivePower (Var) 33 ElectricalMeasurement.Delivered+ReceivedApparentEnergyPhsA (VAh) ElectricalMeasurement.RmsApparentPowerPhsA (VA) 34 ElectricalMeasurement.Delivered-ReceivedApparentEnergyPhsA (VAh) ElectricalMeasurement.RmsApparentPowerPhsA (VA) 35 ElectricalMeasurement.DeliveredApparentEnergyPhsA (VAh) ElectricalMeasurement.RmsApparentPowerPhsA (VA) 36 ElectricalMeasurement.ReceivedApparentEnergyPhsA (VAh) ElectricalMeasurement.RmsApparentPowerPhsA (VA) 37 ElectricalMeasurement.Delivered+ReceivedApparentEnergyPhsB (VAh) ElectricalMeasurement.RmsApparentPowerPhsB (VA) 38 ElectricalMeasurement.Delivered-ReceivedApparentEnergyPhsB (VAh) ElectricalMeasurement.RmsApparentPowerPhsB (VA) 39 ElectricalMeasurement.DeliveredApparentEnergyPhsB (VAh) ElectricalMeasurement.RmsApparentPowerPhsB (VA) 40 ElectricalMeasurement.ReceivedApparentEnergyPhsB (VAh) ElectricalMeasurement.RmsApparentPowerPhsB (VA) 41 ElectricalMeasurement.Delivered+ReceivedApparentEnergyPhsC (VAh) ElectricalMeasurement.RmsApparentPowerPhsC (VA) 42 ElectricalMeasurement.Delivered-ReceivedApparentEnergyPhsC (VAh) ElectricalMeasurement.RmsApparentPowerPhsC (VA) 43 ElectricalMeasurement.DeliveredApparentEnergyPhsC (VAh) ElectricalMeasurement.RmsApparentPowerPhsC (VA) 44 ElectricalMeasurement.ReceivedApparentEnergyPhsC (VAh) ElectricalMeasurement.RmsApparentPowerPhsC (VA) 45 ElectricalMeasurement.TotalDelivered+ReceivedApparentEnergy (VAh) ElectricalMeasurement.TotalRmsApparentPower (VA) 46 ElectricalMeasurement.TotalDelivered-ReceivedApparentEnergy (VAh) ElectricalMeasurement.TotalRmsApparentPower (VA) 47 ElectricalMeasurement.TotalDeliveredApparentEnergy (VAh) ElectricalMeasurement.TotalRmsApparentPower (VA) 48 ElectricalMeasurement.TotalReceivedApparentEnergy (VAh) ElectricalMeasurement.TotalRmsApparentPower (VA) 49 WaterVolume (m³) WaterFlowRate ( m³/h) 50 GasVolume (m³) GasFlowRate ( m³/h) 51 HeatEnergy (Wh) HeatPower (W) 52 ChilledEnergy (Wh) ChilledPower (W) 53 Custom Custom
Local Digital Inputs | 0x0494 | 1173 | 2 | R | - | - | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Measured flow value on DI1 if DI1 mode is set to Pulse. The unit of the measured flow value depends on the DI1 configuration 0 None (None/empty) None/empty (None/empty) 1 ElectricalMeasurement.Delivered+ReceivedActiveEnergyPhsA (Wh) ElectricalMeasurement.RmsActivePowerPhsA (W) 2 ElectricalMeasurement.Delivered-ReceivedActiveEnergyPhsA (Wh) ElectricalMeasurement.RmsActivePowerPhsA (W) 3 ElectricalMeasurement.DeliveredActiveEnergyPhsA (Wh) ElectricalMeasurement.RmsActivePowerPhsA (W) 4 ElectricalMeasurement.ReceivedActiveEnergyPhsA (Wh) ElectricalMeasurement.RmsActivePowerPhsA (W) 5 ElectricalMeasurement.Delivered+ReceivedActiveEnergyPhsB (Wh) ElectricalMeasurement.RmsActivePowerPhsB (W) 6 ElectricalMeasurement.Delivered-ReceivedActiveEnergyPhsB (Wh) ElectricalMeasurement.RmsActivePowerPhsB (W) 7 ElectricalMeasurement.DeliveredActiveEnergyPhsB (Wh) ElectricalMeasurement.RmsActivePowerPhsB (W) 8 ElectricalMeasurement.ReceivedActiveEnergyPhsB (Wh) ElectricalMeasurement.RmsActivePowerPhsB (W) 9 ElectricalMeasurement.Delivered+ReceivedActiveEnergyPhsC (Wh) ElectricalMeasurement.RmsActivePowerPhsC (W) 10 ElectricalMeasurement.Delivered-ReceivedActiveEnergyPhsC (Wh) ElectricalMeasurement.RmsActivePowerPhsC (W) 11 ElectricalMeasurement.DeliveredActiveEnergyPhsC (Wh) ElectricalMeasurement.RmsActivePowerPhsC (W) 12 ElectricalMeasurement.ReceivedActiveEnergyPhsC (Wh) ElectricalMeasurement.RmsActivePowerPhsC (W) 13 ElectricalMeasurement.TotalDelivered+ReceivedActiveEnergy (Wh) ElectricalMeasurement.TotalRmsActivePower (W) 14 ElectricalMeasurement.TotalDelivered-ReceivedActiveEnergy (Wh) ElectricalMeasurement.TotalRmsActivePower (W) 15 ElectricalMeasurement.TotalDeliveredActiveEnergy (Wh) ElectricalMeasurement.TotalRmsActivePower (W) 16 ElectricalMeasurement.TotalReceivedActiveEnergy (Wh) ElectricalMeasurement.TotalRmsActivePower (W) 17 ElectricalMeasurement.Delivered+ReceivedReactiveEnergyPhsA (Varh) ElectricalMeasurement.RmsReactivePowerPhsA (Var) 18 ElectricalMeasurement.Delivered-ReceivedReactiveEnergyPhsA (Varh) ElectricalMeasurement.RmsReactivePowerPhsA (Var) 19 ElectricalMeasurement.DeliveredReactiveEnergyPhsA (Varh) ElectricalMeasurement.RmsReactivePowerPhsA (Var) 20 ElectricalMeasurement.ReceivedReactiveEnergyPhsA (Varh) ElectricalMeasurement.RmsReactivePowerPhsA (Var) 21 ElectricalMeasurement.Delivered+ReceivedReactiveEnergyPhsB (Varh) ElectricalMeasurement.RmsReactivePowerPhsB (Var) 22 ElectricalMeasurement.Delivered-ReceivedReactiveEnergyPhsB (Varh) ElectricalMeasurement.RmsReactivePowerPhsB (Var) 23 ElectricalMeasurement.DeliveredReactiveEnergyPhsB (Varh) ElectricalMeasurement.RmsReactivePowerPhsB (Var) 24 ElectricalMeasurement.ReceivedReactiveEnergyPhsB (Varh) ElectricalMeasurement.RmsReactivePowerPhsB (Var) 25 ElectricalMeasurement.Delivered+ReceivedReactiveEnergyPhsC (Varh) ElectricalMeasurement.RmsReactivePowerPhsC (Var) 26 ElectricalMeasurement.Delivered-ReceivedReactiveEnergyPhsC (Varh) ElectricalMeasurement.RmsReactivePowerPhsC (Var) 27 ElectricalMeasurement.DeliveredReactiveEnergyPhsC (Varh) ElectricalMeasurement.RmsReactivePowerPhsC (Var) 28 ElectricalMeasurement.ReceivedReactiveEnergyPhsC (Varh) ElectricalMeasurement.RmsReactivePowerPhsC (Var) 29 ElectricalMeasurement.TotalDelivered+ReceivedReactiveEnergy (Varh) ElectricalMeasurement.TotalRmsReactivePower (Var) 30 ElectricalMeasurement.TotalDelivered-ReceivedReactiveEnergy (Varh) ElectricalMeasurement.TotalRmsReactivePower (Var) 31 ElectricalMeasurement.TotalDeliveredReactiveEnergy (Varh) ElectricalMeasurement.TotalRmsReactivePower (Var) 32 ElectricalMeasurement.TotalReceivedReactiveEnergy (Varh) ElectricalMeasurement.TotalRmsReactivePower (Var) 33 ElectricalMeasurement.Delivered+ReceivedApparentEnergyPhsA (VAh) ElectricalMeasurement.RmsApparentPowerPhsA (VA) 34 ElectricalMeasurement.Delivered-ReceivedApparentEnergyPhsA (VAh) ElectricalMeasurement.RmsApparentPowerPhsA (VA) 35 ElectricalMeasurement.DeliveredApparentEnergyPhsA (VAh) ElectricalMeasurement.RmsApparentPowerPhsA (VA) 36 ElectricalMeasurement.ReceivedApparentEnergyPhsA (VAh) ElectricalMeasurement.RmsApparentPowerPhsA (VA) 37 ElectricalMeasurement.Delivered+ReceivedApparentEnergyPhsB (VAh) ElectricalMeasurement.RmsApparentPowerPhsB (VA) 38 ElectricalMeasurement.Delivered-ReceivedApparentEnergyPhsB (VAh) ElectricalMeasurement.RmsApparentPowerPhsB (VA) 39 ElectricalMeasurement.DeliveredApparentEnergyPhsB (VAh) ElectricalMeasurement.RmsApparentPowerPhsB (VA) 40 ElectricalMeasurement.ReceivedApparentEnergyPhsB (VAh) ElectricalMeasurement.RmsApparentPowerPhsB (VA) 41 ElectricalMeasurement.Delivered+ReceivedApparentEnergyPhsC (VAh) ElectricalMeasurement.RmsApparentPowerPhsC (VA) 42 ElectricalMeasurement.Delivered-ReceivedApparentEnergyPhsC (VAh) ElectricalMeasurement.RmsApparentPowerPhsC (VA) 43 ElectricalMeasurement.DeliveredApparentEnergyPhsC (VAh) ElectricalMeasurement.RmsApparentPowerPhsC (VA) 44 ElectricalMeasurement.ReceivedApparentEnergyPhsC (VAh) ElectricalMeasurement.RmsApparentPowerPhsC (VA) 45 ElectricalMeasurement.TotalDelivered+ReceivedApparentEnergy (VAh) ElectricalMeasurement.TotalRmsApparentPower (VA) 46 ElectricalMeasurement.TotalDelivered-ReceivedApparentEnergy (VAh) ElectricalMeasurement.TotalRmsApparentPower (VA) 47 ElectricalMeasurement.TotalDeliveredApparentEnergy (VAh) ElectricalMeasurement.TotalRmsApparentPower (VA) 48 ElectricalMeasurement.TotalReceivedApparentEnergy (VAh) ElectricalMeasurement.TotalRmsApparentPower (VA) 49 WaterVolume (m³) WaterFlowRate ( m³/h) 50 GasVolume (m³) GasFlowRate ( m³/h) 51 HeatEnergy (Wh) HeatPower (W) 52 ChilledEnergy (Wh) ChilledPower (W) 53 Custom Custom
Local Digital Inputs | 0x0496 | 1175 | 2 | R | - | - | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Measured flow value on DI2 if DI2 mode is set to Pulse. The unit of the measured flow value depends on the DI2 configuration 0 None (None/empty) None/empty (None/empty) 1 ElectricalMeasurement.Delivered+ReceivedActiveEnergyPhsA (Wh) ElectricalMeasurement.RmsActivePowerPhsA (W) 2 ElectricalMeasurement.Delivered-ReceivedActiveEnergyPhsA (Wh) ElectricalMeasurement.RmsActivePowerPhsA (W) 3 ElectricalMeasurement.DeliveredActiveEnergyPhsA (Wh) ElectricalMeasurement.RmsActivePowerPhsA (W) 4 ElectricalMeasurement.ReceivedActiveEnergyPhsA (Wh) ElectricalMeasurement.RmsActivePowerPhsA (W) 5 ElectricalMeasurement.Delivered+ReceivedActiveEnergyPhsB (Wh) ElectricalMeasurement.RmsActivePowerPhsB (W) 6 ElectricalMeasurement.Delivered-ReceivedActiveEnergyPhsB (Wh) ElectricalMeasurement.RmsActivePowerPhsB (W) 7 ElectricalMeasurement.DeliveredActiveEnergyPhsB (Wh) ElectricalMeasurement.RmsActivePowerPhsB (W) 8 ElectricalMeasurement.ReceivedActiveEnergyPhsB (Wh) ElectricalMeasurement.RmsActivePowerPhsB (W) 9 ElectricalMeasurement.Delivered+ReceivedActiveEnergyPhsC (Wh) ElectricalMeasurement.RmsActivePowerPhsC (W) 10 ElectricalMeasurement.Delivered-ReceivedActiveEnergyPhsC (Wh) ElectricalMeasurement.RmsActivePowerPhsC (W) 11 ElectricalMeasurement.DeliveredActiveEnergyPhsC (Wh) ElectricalMeasurement.RmsActivePowerPhsC (W) 12 ElectricalMeasurement.ReceivedActiveEnergyPhsC (Wh) ElectricalMeasurement.RmsActivePowerPhsC (W) 13 ElectricalMeasurement.TotalDelivered+ReceivedActiveEnergy (Wh) ElectricalMeasurement.TotalRmsActivePower (W) 14 ElectricalMeasurement.TotalDelivered-ReceivedActiveEnergy (Wh) ElectricalMeasurement.TotalRmsActivePower (W) 15 ElectricalMeasurement.TotalDeliveredActiveEnergy (Wh) ElectricalMeasurement.TotalRmsActivePower (W) 16 ElectricalMeasurement.TotalReceivedActiveEnergy (Wh) ElectricalMeasurement.TotalRmsActivePower (W) 17 ElectricalMeasurement.Delivered+ReceivedReactiveEnergyPhsA (Varh) ElectricalMeasurement.RmsReactivePowerPhsA (Var) 18 ElectricalMeasurement.Delivered-ReceivedReactiveEnergyPhsA (Varh) ElectricalMeasurement.RmsReactivePowerPhsA (Var) 19 ElectricalMeasurement.DeliveredReactiveEnergyPhsA (Varh) ElectricalMeasurement.RmsReactivePowerPhsA (Var) 20 ElectricalMeasurement.ReceivedReactiveEnergyPhsA (Varh) ElectricalMeasurement.RmsReactivePowerPhsA (Var) 21 ElectricalMeasurement.Delivered+ReceivedReactiveEnergyPhsB (Varh) ElectricalMeasurement.RmsReactivePowerPhsB (Var) 22 ElectricalMeasurement.Delivered-ReceivedReactiveEnergyPhsB (Varh) ElectricalMeasurement.RmsReactivePowerPhsB (Var) 23 ElectricalMeasurement.DeliveredReactiveEnergyPhsB (Varh) ElectricalMeasurement.RmsReactivePowerPhsB (Var) 24 ElectricalMeasurement.ReceivedReactiveEnergyPhsB (Varh) ElectricalMeasurement.RmsReactivePowerPhsB (Var) 25 ElectricalMeasurement.Delivered+ReceivedReactiveEnergyPhsC (Varh) ElectricalMeasurement.RmsReactivePowerPhsC (Var) 26 ElectricalMeasurement.Delivered-ReceivedReactiveEnergyPhsC (Varh) ElectricalMeasurement.RmsReactivePowerPhsC (Var) 27 ElectricalMeasurement.DeliveredReactiveEnergyPhsC (Varh) ElectricalMeasurement.RmsReactivePowerPhsC (Var) 28 ElectricalMeasurement.ReceivedReactiveEnergyPhsC (Varh) ElectricalMeasurement.RmsReactivePowerPhsC (Var) 29 ElectricalMeasurement.TotalDelivered+ReceivedReactiveEnergy (Varh) ElectricalMeasurement.TotalRmsReactivePower (Var) 30 ElectricalMeasurement.TotalDelivered-ReceivedReactiveEnergy (Varh) ElectricalMeasurement.TotalRmsReactivePower (Var) 31 ElectricalMeasurement.TotalDeliveredReactiveEnergy (Varh) ElectricalMeasurement.TotalRmsReactivePower (Var) 32 ElectricalMeasurement.TotalReceivedReactiveEnergy (Varh) ElectricalMeasurement.TotalRmsReactivePower (Var) 33 ElectricalMeasurement.Delivered+ReceivedApparentEnergyPhsA (VAh) ElectricalMeasurement.RmsApparentPowerPhsA (VA) 34 ElectricalMeasurement.Delivered-ReceivedApparentEnergyPhsA (VAh) ElectricalMeasurement.RmsApparentPowerPhsA (VA) 35 ElectricalMeasurement.DeliveredApparentEnergyPhsA (VAh) ElectricalMeasurement.RmsApparentPowerPhsA (VA) 36 ElectricalMeasurement.ReceivedApparentEnergyPhsA (VAh) ElectricalMeasurement.RmsApparentPowerPhsA (VA) 37 ElectricalMeasurement.Delivered+ReceivedApparentEnergyPhsB (VAh) ElectricalMeasurement.RmsApparentPowerPhsB (VA) 38 ElectricalMeasurement.Delivered-ReceivedApparentEnergyPhsB (VAh) ElectricalMeasurement.RmsApparentPowerPhsB (VA) 39 ElectricalMeasurement.DeliveredApparentEnergyPhsB (VAh) ElectricalMeasurement.RmsApparentPowerPhsB (VA) 40 ElectricalMeasurement.ReceivedApparentEnergyPhsB (VAh) ElectricalMeasurement.RmsApparentPowerPhsB (VA) 41 ElectricalMeasurement.Delivered+ReceivedApparentEnergyPhsC (VAh) ElectricalMeasurement.RmsApparentPowerPhsC (VA) 42 ElectricalMeasurement.Delivered-ReceivedApparentEnergyPhsC (VAh) ElectricalMeasurement.RmsApparentPowerPhsC (VA) 43 ElectricalMeasurement.DeliveredApparentEnergyPhsC (VAh) ElectricalMeasurement.RmsApparentPowerPhsC (VA) 44 ElectricalMeasurement.ReceivedApparentEnergyPhsC (VAh) ElectricalMeasurement.RmsApparentPowerPhsC (VA) 45 ElectricalMeasurement.TotalDelivered+ReceivedApparentEnergy (VAh) ElectricalMeasurement.TotalRmsApparentPower (VA) 46 ElectricalMeasurement.TotalDelivered-ReceivedApparentEnergy (VAh) ElectricalMeasurement.TotalRmsApparentPower (VA) 47 ElectricalMeasurement.TotalDeliveredApparentEnergy (VAh) ElectricalMeasurement.TotalRmsApparentPower (VA) 48 ElectricalMeasurement.TotalReceivedApparentEnergy (VAh) ElectricalMeasurement.TotalRmsApparentPower (VA) 49 WaterVolume (m³) WaterFlowRate ( m³/h) 50 GasVolume (m³) GasFlowRate ( m³/h) 51 HeatEnergy (Wh) HeatPower (W) 52 ChilledEnergy (Wh) ChilledPower (W) 53 Custom Custom
Local Digital Inputs | 0x04C2 | 1219 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Commodity of device connected to DI1 1. Electricity 2. Gas 3. Fuel oil 4. Air 5. Steam 6. Water 7. Environment 8. Other 9. Custom (Free text to enter): User can enter 10 custom values
Local Digital Inputs | 0x04C3 | 1220 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Commodity of device connected to DI2 1. Electricity 2. Gas 3. Fuel oil 4. Air 5. Steam 6. Water 7. Environment 8. Other 9. Custom (Free text to enter): User can enter 10 custom values
Local Digital Inputs | 0x04C4 | 1221 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Features assigned to digital input: 0 None 1 Custom 2 Circuit breaker status 3 Trip fault (SD) 4 Trip indicator synthesis 5 Trip elec fault (SDE) 6 Trip thermal fault (SDT) 7 Earth leakage fault 8 Ground fault 9 Surge arrester fault 10 Insulation fault 11 Circuit Breaker connected position 12 Circuit Breaker disconnected position 13 Circuit Breaker test position 14 Energy Reduction Maintenance Setting status 15 Door status 17 Drawer connected position 18 Drawer disconnected position 19 Drawer test position 20 Voltage loss 21 Advanced protection 22 Switch position 23 Fuse blown 24 Relay status 25 Trip circuit supervision 26 Emergency stop 27 Watchdog status 28 Source change over - A (Alternate) status 29 Source change over - Off status 30 Source change over - N (Normal) status 31 Motor preheating 32 Motor run 33 Motor start 34 Forced freewheel stop 35 Battery status 36 Battery end of autonomy 37 UPS status 38 UPS running mode 39 Auxiliary supply status 40 Tariff 1 Status 41 Tariff 2 Status 42 Tariff 3 Status 43 Tariff 4 Status 44 Tariff 5 Status 45 Flood detection 46 Under temperature 47 Over temperature 48 Process mode 49 Equipment status 50 Fan status 51 Standard Input Low-High 52 Standard Input 0V-24V 53 Standard Input Disconnected-Off 54 Standard input
Local Digital Inputs | 0x04C5 | 1222 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Features assigned to digital input: 0 None 1 Custom 2 Circuit breaker status 3 Trip fault (SD) 4 Trip indicator synthesis 5 Trip elec fault (SDE) 6 Trip thermal fault (SDT) 7 Earth leakage fault 8 Ground fault 9 Surge arrester fault 10 Insulation fault 11 Circuit Breaker connected position 12 Circuit Breaker disconnected position 13 Circuit Breaker test position 14 Energy Reduction Maintenance Setting status 15 Door status 17 Drawer connected position 18 Drawer disconnected position 19 Drawer test position 20 Voltage loss 21 Advanced protection 22 Switch position 23 Fuse blown 24 Relay status 25 Trip circuit supervision 26 Emergency stop 27 Watchdog status 28 Source change over - A (Alternate) status 29 Source change over - Off status 30 Source change over - N (Normal) status 31 Motor preheating 32 Motor run 33 Motor start 34 Forced freewheel stop 35 Battery status 36 Battery end of autonomy 37 UPS status 38 UPS running mode 39 Auxiliary supply status 40 Tariff 1 Status 41 Tariff 2 Status 42 Tariff 3 Status 43 Tariff 4 Status 44 Tariff 5 Status 45 Flood detection 46 Under temperature 47 Over temperature 48 Process mode 49 Equipment status 50 Fan status 51 Standard Input Low-High 52 Standard Input 0V-24V 53 Standard Input Disconnected-Off 54 Standard input
Local Digital Inputs | 0x04C6 | 1223 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Digital input DI1 electrical status. Indicates the electrical status of the input, regardless of the assignment reference & polarity • 0 = Low level • 1 = High level
Local Digital Inputs | 0x04C7 | 1224 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Digital input DI2 electrical status. Indicates the electrical status of the input, regardless of the assignment reference & polarity • 0 = Low level • 1 = High level
Local Digital Inputs | 0x04C8 | 1225 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Polarity of the Digital Input DI1 Meaning of input: /0 for inactive/1 for active/: // Input Electrical status = 0V --> input is inactive (eg: Trip fault (SD) = ‘No Fault’ / Motor run = ‘Off’) // // Input Electrical status = 230V or 24V --> input is active (eg: Trip fault (SD) = ‘Fault’ / Motor run = ‘Run’) // or Meaning of input: /1 for inactive/0 for active/ // Input Electrical status = 0V --> input is active (eg: Trip fault (SD) = ‘Fault’ / Motor run = ‘Run’) // // Input Electrical status = 230V or 24 V --> input is inactive (eg: Trip fault (SD) = ‘No Fault’ / Motor run = ‘Off’) //
Local Digital Inputs | 0x04C9 | 1226 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Polarity of the Digital Input DI2 Meaning of input: /0 for inactive/1 for active/: // Input Electrical status = 0V --> input is inactive (eg: Trip fault (SD) = ‘No Fault’ / Motor run = ‘Off’) // // Input Electrical status = 230V or 24V --> input is active (eg: Trip fault (SD) = ‘Fault’ / Motor run = ‘Run’) // or Meaning of input: /1 for inactive/0 for active/ // Input Electrical status = 0V --> input is active (eg: Trip fault (SD) = ‘Fault’ / Motor run = ‘Run’) // // Input Electrical status = 230V or 24 V --> input is inactive (eg: Trip fault (SD) = ‘No Fault’ / Motor run = ‘Off’) //
Local Digital Inputs | 0x04CA | 1227 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text giving the context of use of the Digital Input DI1 when DI1 is defined as 'Custom'
Local Digital Inputs | 0x04D4 | 1237 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text giving the context of use of the Digital Input DI2 when DI2 is defined as 'Custom'
Local Digital Inputs | 0x04DE | 1247 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text defining the inactive value of the Digital Input DI1 when DI1 is defined as 'Custom'
Local Digital Inputs | 0x04E8 | 1257 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text defining the inactive value of the Digital Input DI2 when DI2 is defined as 'Custom'
Local Digital Inputs | 0x04F2 | 1267 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text defining the active value of the Digital Input DI1 when DI1 is defined as 'Custom'
Local Digital Inputs | 0x04FC | 1277 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text defining the active value of the Digital Input DI2 when DI2 is defined as 'Custom'
Local Digital Inputs | 0x0506 | 1287 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Feature assigned to digital input (Accumulated value + unit, and associated flow value + flow unit) 0 None (None/empty) None/empty (None/empty) 1 ElectricalMeasurement.Delivered+ReceivedActiveEnergyPhsA (Wh) ElectricalMeasurement.RmsActivePowerPhsA (W) 2 ElectricalMeasurement.Delivered-ReceivedActiveEnergyPhsA (Wh) ElectricalMeasurement.RmsActivePowerPhsA (W) 3 ElectricalMeasurement.DeliveredActiveEnergyPhsA (Wh) ElectricalMeasurement.RmsActivePowerPhsA (W) 4 ElectricalMeasurement.ReceivedActiveEnergyPhsA (Wh) ElectricalMeasurement.RmsActivePowerPhsA (W) 5 ElectricalMeasurement.Delivered+ReceivedActiveEnergyPhsB (Wh) ElectricalMeasurement.RmsActivePowerPhsB (W) 6 ElectricalMeasurement.Delivered-ReceivedActiveEnergyPhsB (Wh) ElectricalMeasurement.RmsActivePowerPhsB (W) 7 ElectricalMeasurement.DeliveredActiveEnergyPhsB (Wh) ElectricalMeasurement.RmsActivePowerPhsB (W) 8 ElectricalMeasurement.ReceivedActiveEnergyPhsB (Wh) ElectricalMeasurement.RmsActivePowerPhsB (W) 9 ElectricalMeasurement.Delivered+ReceivedActiveEnergyPhsC (Wh) ElectricalMeasurement.RmsActivePowerPhsC (W) 10 ElectricalMeasurement.Delivered-ReceivedActiveEnergyPhsC (Wh) ElectricalMeasurement.RmsActivePowerPhsC (W) 11 ElectricalMeasurement.DeliveredActiveEnergyPhsC (Wh) ElectricalMeasurement.RmsActivePowerPhsC (W) 12 ElectricalMeasurement.ReceivedActiveEnergyPhsC (Wh) ElectricalMeasurement.RmsActivePowerPhsC (W) 13 ElectricalMeasurement.TotalDelivered+ReceivedActiveEnergy (Wh) ElectricalMeasurement.TotalRmsActivePower (W) 14 ElectricalMeasurement.TotalDelivered-ReceivedActiveEnergy (Wh) ElectricalMeasurement.TotalRmsActivePower (W) 15 ElectricalMeasurement.TotalDeliveredActiveEnergy (Wh) ElectricalMeasurement.TotalRmsActivePower (W) 16 ElectricalMeasurement.TotalReceivedActiveEnergy (Wh) ElectricalMeasurement.TotalRmsActivePower (W) 17 ElectricalMeasurement.Delivered+ReceivedReactiveEnergyPhsA (Varh) ElectricalMeasurement.RmsReactivePowerPhsA (Var) 18 ElectricalMeasurement.Delivered-ReceivedReactiveEnergyPhsA (Varh) ElectricalMeasurement.RmsReactivePowerPhsA (Var) 19 ElectricalMeasurement.DeliveredReactiveEnergyPhsA (Varh) ElectricalMeasurement.RmsReactivePowerPhsA (Var) 20 ElectricalMeasurement.ReceivedReactiveEnergyPhsA (Varh) ElectricalMeasurement.RmsReactivePowerPhsA (Var) 21 ElectricalMeasurement.Delivered+ReceivedReactiveEnergyPhsB (Varh) ElectricalMeasurement.RmsReactivePowerPhsB (Var) 22 ElectricalMeasurement.Delivered-ReceivedReactiveEnergyPhsB (Varh) ElectricalMeasurement.RmsReactivePowerPhsB (Var) 23 ElectricalMeasurement.DeliveredReactiveEnergyPhsB (Varh) ElectricalMeasurement.RmsReactivePowerPhsB (Var) 24 ElectricalMeasurement.ReceivedReactiveEnergyPhsB (Varh) ElectricalMeasurement.RmsReactivePowerPhsB (Var) 25 ElectricalMeasurement.Delivered+ReceivedReactiveEnergyPhsC (Varh) ElectricalMeasurement.RmsReactivePowerPhsC (Var) 26 ElectricalMeasurement.Delivered-ReceivedReactiveEnergyPhsC (Varh) ElectricalMeasurement.RmsReactivePowerPhsC (Var) 27 ElectricalMeasurement.DeliveredReactiveEnergyPhsC (Varh) ElectricalMeasurement.RmsReactivePowerPhsC (Var) 28 ElectricalMeasurement.ReceivedReactiveEnergyPhsC (Varh) ElectricalMeasurement.RmsReactivePowerPhsC (Var) 29 ElectricalMeasurement.TotalDelivered+ReceivedReactiveEnergy (Varh) ElectricalMeasurement.TotalRmsReactivePower (Var) 30 ElectricalMeasurement.TotalDelivered-ReceivedReactiveEnergy (Varh) ElectricalMeasurement.TotalRmsReactivePower (Var) 31 ElectricalMeasurement.TotalDeliveredReactiveEnergy (Varh) ElectricalMeasurement.TotalRmsReactivePower (Var) 32 ElectricalMeasurement.TotalReceivedReactiveEnergy (Varh) ElectricalMeasurement.TotalRmsReactivePower (Var) 33 ElectricalMeasurement.Delivered+ReceivedApparentEnergyPhsA (VAh) ElectricalMeasurement.RmsApparentPowerPhsA (VA) 34 ElectricalMeasurement.Delivered-ReceivedApparentEnergyPhsA (VAh) ElectricalMeasurement.RmsApparentPowerPhsA (VA) 35 ElectricalMeasurement.DeliveredApparentEnergyPhsA (VAh) ElectricalMeasurement.RmsApparentPowerPhsA (VA) 36 ElectricalMeasurement.ReceivedApparentEnergyPhsA (VAh) ElectricalMeasurement.RmsApparentPowerPhsA (VA) 37 ElectricalMeasurement.Delivered+ReceivedApparentEnergyPhsB (VAh) ElectricalMeasurement.RmsApparentPowerPhsB (VA) 38 ElectricalMeasurement.Delivered-ReceivedApparentEnergyPhsB (VAh) ElectricalMeasurement.RmsApparentPowerPhsB (VA) 39 ElectricalMeasurement.DeliveredApparentEnergyPhsB (VAh) ElectricalMeasurement.RmsApparentPowerPhsB (VA) 40 ElectricalMeasurement.ReceivedApparentEnergyPhsB (VAh) ElectricalMeasurement.RmsApparentPowerPhsB (VA) 41 ElectricalMeasurement.Delivered+ReceivedApparentEnergyPhsC (VAh) ElectricalMeasurement.RmsApparentPowerPhsC (VA) 42 ElectricalMeasurement.Delivered-ReceivedApparentEnergyPhsC (VAh) ElectricalMeasurement.RmsApparentPowerPhsC (VA) 43 ElectricalMeasurement.DeliveredApparentEnergyPhsC (VAh) ElectricalMeasurement.RmsApparentPowerPhsC (VA) 44 ElectricalMeasurement.ReceivedApparentEnergyPhsC (VAh) ElectricalMeasurement.RmsApparentPowerPhsC (VA) 45 ElectricalMeasurement.TotalDelivered+ReceivedApparentEnergy (VAh) ElectricalMeasurement.TotalRmsApparentPower (VA) 46 ElectricalMeasurement.TotalDelivered-ReceivedApparentEnergy (VAh) ElectricalMeasurement.TotalRmsApparentPower (VA) 47 ElectricalMeasurement.TotalDeliveredApparentEnergy (VAh) ElectricalMeasurement.TotalRmsApparentPower (VA) 48 ElectricalMeasurement.TotalReceivedApparentEnergy (VAh) ElectricalMeasurement.TotalRmsApparentPower (VA) 49 WaterVolume (m³) WaterFlowRate ( m³/h) 50 GasVolume (m³) GasFlowRate ( m³/h) 51 HeatEnergy (Wh) HeatPower (W) 52 ChilledEnergy (Wh) ChilledPower (W) 53 Custom Custom
Local Digital Inputs | 0x0507 | 1288 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Feature assigned to digital input (Accumulated value + unit, and associated flow value + flow unit) 0 None (None/empty) None/empty (None/empty) 1 ElectricalMeasurement.Delivered+ReceivedActiveEnergyPhsA (Wh) ElectricalMeasurement.RmsActivePowerPhsA (W) 2 ElectricalMeasurement.Delivered-ReceivedActiveEnergyPhsA (Wh) ElectricalMeasurement.RmsActivePowerPhsA (W) 3 ElectricalMeasurement.DeliveredActiveEnergyPhsA (Wh) ElectricalMeasurement.RmsActivePowerPhsA (W) 4 ElectricalMeasurement.ReceivedActiveEnergyPhsA (Wh) ElectricalMeasurement.RmsActivePowerPhsA (W) 5 ElectricalMeasurement.Delivered+ReceivedActiveEnergyPhsB (Wh) ElectricalMeasurement.RmsActivePowerPhsB (W) 6 ElectricalMeasurement.Delivered-ReceivedActiveEnergyPhsB (Wh) ElectricalMeasurement.RmsActivePowerPhsB (W) 7 ElectricalMeasurement.DeliveredActiveEnergyPhsB (Wh) ElectricalMeasurement.RmsActivePowerPhsB (W) 8 ElectricalMeasurement.ReceivedActiveEnergyPhsB (Wh) ElectricalMeasurement.RmsActivePowerPhsB (W) 9 ElectricalMeasurement.Delivered+ReceivedActiveEnergyPhsC (Wh) ElectricalMeasurement.RmsActivePowerPhsC (W) 10 ElectricalMeasurement.Delivered-ReceivedActiveEnergyPhsC (Wh) ElectricalMeasurement.RmsActivePowerPhsC (W) 11 ElectricalMeasurement.DeliveredActiveEnergyPhsC (Wh) ElectricalMeasurement.RmsActivePowerPhsC (W) 12 ElectricalMeasurement.ReceivedActiveEnergyPhsC (Wh) ElectricalMeasurement.RmsActivePowerPhsC (W) 13 ElectricalMeasurement.TotalDelivered+ReceivedActiveEnergy (Wh) ElectricalMeasurement.TotalRmsActivePower (W) 14 ElectricalMeasurement.TotalDelivered-ReceivedActiveEnergy (Wh) ElectricalMeasurement.TotalRmsActivePower (W) 15 ElectricalMeasurement.TotalDeliveredActiveEnergy (Wh) ElectricalMeasurement.TotalRmsActivePower (W) 16 ElectricalMeasurement.TotalReceivedActiveEnergy (Wh) ElectricalMeasurement.TotalRmsActivePower (W) 17 ElectricalMeasurement.Delivered+ReceivedReactiveEnergyPhsA (Varh) ElectricalMeasurement.RmsReactivePowerPhsA (Var) 18 ElectricalMeasurement.Delivered-ReceivedReactiveEnergyPhsA (Varh) ElectricalMeasurement.RmsReactivePowerPhsA (Var) 19 ElectricalMeasurement.DeliveredReactiveEnergyPhsA (Varh) ElectricalMeasurement.RmsReactivePowerPhsA (Var) 20 ElectricalMeasurement.ReceivedReactiveEnergyPhsA (Varh) ElectricalMeasurement.RmsReactivePowerPhsA (Var) 21 ElectricalMeasurement.Delivered+ReceivedReactiveEnergyPhsB (Varh) ElectricalMeasurement.RmsReactivePowerPhsB (Var) 22 ElectricalMeasurement.Delivered-ReceivedReactiveEnergyPhsB (Varh) ElectricalMeasurement.RmsReactivePowerPhsB (Var) 23 ElectricalMeasurement.DeliveredReactiveEnergyPhsB (Varh) ElectricalMeasurement.RmsReactivePowerPhsB (Var) 24 ElectricalMeasurement.ReceivedReactiveEnergyPhsB (Varh) ElectricalMeasurement.RmsReactivePowerPhsB (Var) 25 ElectricalMeasurement.Delivered+ReceivedReactiveEnergyPhsC (Varh) ElectricalMeasurement.RmsReactivePowerPhsC (Var) 26 ElectricalMeasurement.Delivered-ReceivedReactiveEnergyPhsC (Varh) ElectricalMeasurement.RmsReactivePowerPhsC (Var) 27 ElectricalMeasurement.DeliveredReactiveEnergyPhsC (Varh) ElectricalMeasurement.RmsReactivePowerPhsC (Var) 28 ElectricalMeasurement.ReceivedReactiveEnergyPhsC (Varh) ElectricalMeasurement.RmsReactivePowerPhsC (Var) 29 ElectricalMeasurement.TotalDelivered+ReceivedReactiveEnergy (Varh) ElectricalMeasurement.TotalRmsReactivePower (Var) 30 ElectricalMeasurement.TotalDelivered-ReceivedReactiveEnergy (Varh) ElectricalMeasurement.TotalRmsReactivePower (Var) 31 ElectricalMeasurement.TotalDeliveredReactiveEnergy (Varh) ElectricalMeasurement.TotalRmsReactivePower (Var) 32 ElectricalMeasurement.TotalReceivedReactiveEnergy (Varh) ElectricalMeasurement.TotalRmsReactivePower (Var) 33 ElectricalMeasurement.Delivered+ReceivedApparentEnergyPhsA (VAh) ElectricalMeasurement.RmsApparentPowerPhsA (VA) 34 ElectricalMeasurement.Delivered-ReceivedApparentEnergyPhsA (VAh) ElectricalMeasurement.RmsApparentPowerPhsA (VA) 35 ElectricalMeasurement.DeliveredApparentEnergyPhsA (VAh) ElectricalMeasurement.RmsApparentPowerPhsA (VA) 36 ElectricalMeasurement.ReceivedApparentEnergyPhsA (VAh) ElectricalMeasurement.RmsApparentPowerPhsA (VA) 37 ElectricalMeasurement.Delivered+ReceivedApparentEnergyPhsB (VAh) ElectricalMeasurement.RmsApparentPowerPhsB (VA) 38 ElectricalMeasurement.Delivered-ReceivedApparentEnergyPhsB (VAh) ElectricalMeasurement.RmsApparentPowerPhsB (VA) 39 ElectricalMeasurement.DeliveredApparentEnergyPhsB (VAh) ElectricalMeasurement.RmsApparentPowerPhsB (VA) 40 ElectricalMeasurement.ReceivedApparentEnergyPhsB (VAh) ElectricalMeasurement.RmsApparentPowerPhsB (VA) 41 ElectricalMeasurement.Delivered+ReceivedApparentEnergyPhsC (VAh) ElectricalMeasurement.RmsApparentPowerPhsC (VA) 42 ElectricalMeasurement.Delivered-ReceivedApparentEnergyPhsC (VAh) ElectricalMeasurement.RmsApparentPowerPhsC (VA) 43 ElectricalMeasurement.DeliveredApparentEnergyPhsC (VAh) ElectricalMeasurement.RmsApparentPowerPhsC (VA) 44 ElectricalMeasurement.ReceivedApparentEnergyPhsC (VAh) ElectricalMeasurement.RmsApparentPowerPhsC (VA) 45 ElectricalMeasurement.TotalDelivered+ReceivedApparentEnergy (VAh) ElectricalMeasurement.TotalRmsApparentPower (VA) 46 ElectricalMeasurement.TotalDelivered-ReceivedApparentEnergy (VAh) ElectricalMeasurement.TotalRmsApparentPower (VA) 47 ElectricalMeasurement.TotalDeliveredApparentEnergy (VAh) ElectricalMeasurement.TotalRmsApparentPower (VA) 48 ElectricalMeasurement.TotalReceivedApparentEnergy (VAh) ElectricalMeasurement.TotalRmsApparentPower (VA) 49 WaterVolume (m³) WaterFlowRate ( m³/h) 50 GasVolume (m³) GasFlowRate ( m³/h) 51 HeatEnergy (Wh) HeatPower (W) 52 ChilledEnergy (Wh) ChilledPower (W) 53 Custom Custom
Local Digital Inputs | 0x0508 | 1289 | 20 | R | - | - | ASCII |  | 0x00000000000000000000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Custom Metering accumulated name for DI1. Only applicable if DI mode is "Pulse"
Local Digital Inputs | 0x051C | 1309 | 20 | R | - | - | ASCII |  | 0x00000000000000000000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Custom Metering accumulated name for DI2 Only applicable if DI mode is "Pulse"
Local Digital Inputs | 0x0530 | 1329 | 20 | R | - | - | ASCII |  | 0x00000000000000000000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Metering accumulated custom unit for DI1. Unit defined at Commissioning time. Used only if unit is custom. Only applicable if DI mode is "Pulse"
Local Digital Inputs | 0x0544 | 1349 | 20 | R | - | - | ASCII |  | 0x00000000000000000000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Metering accumulated custom unit for DI2. Unit defined at Commissioning time. Used only if unit is custom. Only applicable if DI mode is "Pulse"
Local Digital Inputs | 0x0558 | 1369 | 20 | R | - | - | ASCII |  | 0x00000000000000000000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Custom Flow name for DI1. Only applicable if DI mode is "Pulse"
Local Digital Inputs | 0x056C | 1389 | 20 | R | - | - | ASCII |  | 0x00000000000000000000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Custom Flow name for DI2. Only applicable if DI mode is "Pulse"
Local Digital Inputs | 0x0580 | 1409 | 20 | R | - | - | ASCII |  | 0x00000000000000000000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Measured Flow custom unit for DI1. Unit defined at Commissioning time. Used only if unit is custom. Only applicable if DI mode is "Pulse"
Local Digital Inputs | 0x0594 | 1429 | 20 | R | - | - | ASCII |  | 0x00000000000000000000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Measured Flow custom unit for DI2. Unit defined at Commissioning time. Used only if unit is custom. Only applicable if DI mode is "Pulse"
Local Digital Inputs | 0x05A8 | 1449 | 2 | R | - | - | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Measured volume value on DI1 if DI1 mode is set to Pulse and DI1 configuration equals V_gaz or V_water. The unit of the measured volume value is in (m³) for: WaterVolume(m³) and GasVolume(m³)
Local Digital Inputs | 0x05AA | 1451 | 2 | R | - | - | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Measured volume value on DI2 if DI2 mode is set to Pulse and DI2 configuration equals V_gaz or V_water. The unit of the measured volume value is in (m³) for: WaterVolume(m³) and GasVolume(m³)
Identification | 0x1605 | 5638 | 32 | R | - | - | ASCII |  | 0x00000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | EcoStruxure Panel Server user application name
Exiway Link Control | 0x2710 | 10001 | 1 | RW | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4, 16 | Synchronize (reset) all the timers of the Exiway Devices connected to the PaS: ENUM { Sync = 1, }
Modbus TCP/IP Server Configuration | 0x306F | 12400 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Modbus ID of PaS
Modbus Serial Configuration | 0x3070 | 12401 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Modbus Parity • 1 = No Parity • 2 = Even parity • 3 = Odd parity
Modbus Serial Configuration | 0x3071 | 12402 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Modbus Baud Rate • 3 = 1200 Baud • 4 = 2400 Baud • 5 = 4800 Baud • 6 = 9600 Baud • 7 = 19200 Baud • 8 = 38400 Baud • 9 = 57600 Baud • 10 = 115200 Baud
Modbus Serial Configuration | 0x3072 | 12403 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Number of stop bits • 3 = 1 stop bit • 5 = 2 stop bits
Modbus Serial Configuration | 0x3073 | 12404 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Silent Time after Modbus SL packet end in millisecond: • Default = 5 ms • Min = 0 ms • Max = 10 ms
Modbus Serial Configuration | 0x3074 | 12405 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Delay Between Modbus SL Packets in millisecond: • Default = 50 ms • Min = 0 ms • Max = 100 ms
Modbus Serial Configuration | 0x3075 | 12406 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Connect/Disconnect the RS485 termination resistor: • ON = 1 // Connect • OFF = 0 // Disconnect • Undetermined = 65535 // Invalid value
Modbus Serial Configuration | 0x3076 | 12407 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Transmission Line State • ON = 1 // Connect • OFF = 0 // Disconnect • Undetermined = 65535 // Invalid value
Modbus Serial Client Configuration | 0x3077 | 12408 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Message timeout of modbus SL request • Default = 3000 ms • Min = 100 ms • Max = 10000 ms
Modbus TCP/IP Client Configuration | 0x3078 | 12409 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Timeout of Modbus TCP/IP Client in milliseconds: • Default = 3000 ms • Min = 100 ms • Max = 10000 ms
Modbus TCP/IP Server Configuration | 0x3079 | 12410 | 2 | R | - | - | UINT32 |  | 0xFFFFFFFF | Y | 3, 100-4 | Message timeout of modbus TCP/IP request in milliseconds: • Default = 6000 ms • Min = 1000 ms • Max = 320000 ms
Modbus TCP/IP Client Configuration | 0x307B | 12412 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Message timeout of modbus TCP/IP client request in milliseconds: • Default = 6000 ms • Min = 1000 ms • Max = 20000 ms
Modbus Serial Client, Line Configuration | 0x3084 | 12421 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Modbus Serial Client Configuration of serial line 1 range. The minimum address value of supported addresses (Starting address): • Default = 1
Modbus Serial Client, Line Configuration | 0x3085 | 12422 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Modbus Serial Client Configuration of serial line 1 range. The maximum address value of supported addresses (Ending address): • Default = 199
Modbus Serial Line 2 Configuration | 0x3086 | 12423 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Modbus Parity (Serial Line 2) • 1 = No Parity • 2 = Even parity • 3 = Odd parity
Modbus Serial Line 2 Configuration | 0x3087 | 12424 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Modbus Baud Rate (Serial Line 2) • 3 = 1200 Baud • 4 = 2400 Baud • 5 = 4800 Baud • 6 = 9600 Baud • 7 = 19200 Baud • 8 = 38400 Baud • 9 = 57600 Baud • 10 = 115200 Baud
Modbus Serial Line 2 Configuration | 0x3088 | 12425 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Number of stop bits (Serial Line 2) • 3 = 1 stop bit • 5 = 2 stop bits
Modbus Serial Line 2 Configuration | 0x3089 | 12426 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Silent Time after Modbus SL packet end in millisecond (Serial Line 2): • Default = 5 ms • Min = 0 ms • Max = 10 ms
Modbus Serial Line 2 Configuration | 0x308A | 12427 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Delay Between Modbus SL Packets in millisecond (Serial Line 2): • Default = 50 ms • Min = 0 ms • Max = 100 ms
Modbus Serial Line 2 Configuration | 0x308B | 12428 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Connect/Disconnect the RS485 termination resistor (Serial Line 2): • ON = 1 // Connect • OFF = 0 // Disconnect • Undetermined = 65535 // Invalid value
Modbus Serial Line 2 Configuration | 0x308C | 12429 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Transmission Line 2 State • ON = 1 // Connect • OFF = 0 // Disconnect • Undetermined = 65535 // Invalid value
Modbus Serial Client, Line 2 Configuration | 0x308D | 12430 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Modbus Serial Client Configuration of serial line 2 range. The minimum address value of supported addresses (Starting address): • Default = 200
Modbus Serial Client, Line 2 Configuration | 0x308E | 12431 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Modbus Serial Client Configuration of serial line 2 range. The maximum address value of supported addresses (Ending address): • Default = 254
Modbus Serial Client, Line 2 Configuration | 0x308F | 12432 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Message timeout of modbus SL Line 2 request • Default = 3000 ms • Min = 100 ms • Max = 10000 ms
Wireless Devices Configuration | 0x754E | 30031 | 2 | R | - | SEC | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Power demand sliding window in seconds for all applicable wireless devices
Wireless Devices Configuration | 0x7550 | 30033 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Reset all Peak Active Power Demand of all applicable wireless devices; any value writen in the register will reset Peak Active Power Demand to 0
Identification | 0xF002 | 61443 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | EcoStruxure Panel Server product identifier
Identification | 0xF003 | 61444 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | EcoStruxure Panel Server product model

## Synthesis Table
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description | PTE63-PoTag QO | PTEnergy250_630-PoTag Efram | PTE Rope-PoTag Rope | TH110 | CL110 | CO2 sensors | Temperature sensors TRH | PowerLogic HeatTag | Acti9 Active | Wireless indication auxiliary | Partial Discharge Box | PowerTagC2DI | PowerTagCIO | MasterPacT MTZ Active A | MasterPacT MTZ Active E | ExiwayLight | ZBRT
Identification | 0x0001 | 2 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product identifier
Identification | 0x0002 | 3 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Manufacturer Name - "Schneider Electric"
Identification | 0x0012 | 19 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial Reference of the Gateway - Example "PAS600L"
Identification | 0x0022 | 35 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product Range of the Gateway
Identification | 0x002A | 43 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | "Synthesis Table"
Identification | 0x0032 | 51 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | "Synthesis Table"
Identification | 0x003C | 61 | 17 | R | - | - | ASCII |  | 0x00000000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Vendor URL
Identification | 0x004E | 79 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product identifier of the Gateway
Identification | 0x004F | 80 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Product code of the Gateway
Identification | 0x005F | 96 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware revision of the Gateway
Identification | 0x0065 | 102 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Gateway
Identification | 0x006F | 112 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Gateway
Device Identification | 0x012C | 301 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 1 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x012D | 302 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 2 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x012E | 303 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 3 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x012F | 304 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0130 | 305 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 5 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0131 | 306 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 6 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0132 | 307 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 7 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0133 | 308 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 8 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0134 | 309 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 9 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0135 | 310 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 10 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0136 | 311 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 11 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0137 | 312 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 12 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0138 | 313 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 13 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0139 | 314 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 14 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x013A | 315 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 15 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x013B | 316 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 16 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x013C | 317 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 17 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x013D | 318 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 18 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x013E | 319 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 19 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x013F | 320 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 20 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0140 | 321 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 21 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0141 | 322 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 22 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0142 | 323 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 23 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0143 | 324 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 24 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0144 | 325 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 25 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0145 | 326 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 26 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0146 | 327 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 27 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0147 | 328 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 28 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0148 | 329 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 29 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0149 | 330 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 30 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x014A | 331 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 31 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x014B | 332 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 32 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x014C | 333 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 33 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x014D | 334 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 34 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x014E | 335 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 35 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x014F | 336 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 36 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0150 | 337 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 37 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0151 | 338 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 38 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0152 | 339 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 39 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0153 | 340 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 40 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0154 | 341 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 41 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0155 | 342 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 42 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0156 | 343 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 43 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0157 | 344 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 44 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0158 | 345 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 45 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0159 | 346 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 46 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x015A | 347 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 47 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x015B | 348 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 48 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x015C | 349 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 49 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x015D | 350 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 50 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x015E | 351 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 51 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x015F | 352 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 52 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0160 | 353 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 53 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0161 | 354 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 54 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0162 | 355 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 55 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0163 | 356 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 56 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0164 | 357 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 57 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0165 | 358 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 58 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0166 | 359 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 59 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0167 | 360 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 60 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0168 | 361 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 61 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0169 | 362 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 62 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x016A | 363 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 63 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x016B | 364 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 64 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x016C | 365 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 65 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x016D | 366 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 66 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x016E | 367 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 67 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x016F | 368 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 68 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0170 | 369 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 69 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0171 | 370 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 70 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0172 | 371 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 71 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0173 | 372 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 72 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0174 | 373 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 73 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0175 | 374 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 74 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0176 | 375 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 75 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0177 | 376 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 76 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0178 | 377 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 77 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0179 | 378 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 78 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x017A | 379 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 79 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x017B | 380 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 80 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x017C | 381 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 81 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x017D | 382 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 82 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x017E | 383 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 83 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x017F | 384 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 84 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0180 | 385 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 85 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0181 | 386 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 86 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0182 | 387 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 87 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0183 | 388 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 88 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0184 | 389 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 89 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0185 | 390 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 90 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0186 | 391 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 91 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0187 | 392 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 92 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0188 | 393 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 93 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0189 | 394 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 94 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x018A | 395 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 95 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x018B | 396 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 96 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x018C | 397 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 97 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x018D | 398 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 98 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x018E | 399 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 99 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x018F | 400 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Virtual address of the wireless device 100 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0190 | 401 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 1 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0191 | 402 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 2 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0192 | 403 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 3 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0193 | 404 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0194 | 405 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 5 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0195 | 406 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 6 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0196 | 407 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 7 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0197 | 408 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 8 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0198 | 409 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 9 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0199 | 410 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 10 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x019A | 411 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 11 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x019B | 412 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 12 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x019C | 413 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 13 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x019D | 414 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 14 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x019E | 415 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 15 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x019F | 416 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 16 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01A0 | 417 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 17 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01A1 | 418 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 18 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01A2 | 419 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 19 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01A3 | 420 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 20 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01A4 | 421 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 21 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01A5 | 422 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 22 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01A6 | 423 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 23 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01A7 | 424 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 24 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01A8 | 425 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 25 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01A9 | 426 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 26 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01AA | 427 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 27 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01AB | 428 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 28 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01AC | 429 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 29 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01AD | 430 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 30 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01AE | 431 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 31 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01AF | 432 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 32 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01B0 | 433 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 33 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01B1 | 434 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 34 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01B2 | 435 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 35 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01B3 | 436 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 36 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01B4 | 437 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 37 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01B5 | 438 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 38 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01B6 | 439 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 39 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01B7 | 440 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 40 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01B8 | 441 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 41 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01B9 | 442 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 42 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01BA | 443 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 43 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01BB | 444 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 44 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01BC | 445 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 45 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01BD | 446 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 46 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01BE | 447 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 47 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01BF | 448 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 48 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01C0 | 449 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 49 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01C1 | 450 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 50 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01C2 | 451 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 51 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01C3 | 452 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 52 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01C4 | 453 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 53 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01C5 | 454 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 54 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01C6 | 455 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 55 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01C7 | 456 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 56 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01C8 | 457 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 57 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01C9 | 458 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 58 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01CA | 459 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 59 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01CB | 460 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 60 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01CC | 461 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 61 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01CD | 462 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 62 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01CE | 463 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 63 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01CF | 464 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 64 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01D0 | 465 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 65 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01D1 | 466 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 66 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01D2 | 467 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 67 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01D3 | 468 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 68 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01D4 | 469 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 69 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01D5 | 470 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 70 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01D6 | 471 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 71 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01D7 | 472 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 72 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01D8 | 473 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 73 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01D9 | 474 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 74 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01DA | 475 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 75 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01DB | 476 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 76 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01DC | 477 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 77 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01DD | 478 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 78 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01DE | 479 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 79 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01DF | 480 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 80 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01E0 | 481 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 81 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01E1 | 482 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 82 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01E2 | 483 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 83 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01E3 | 484 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 84 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01E4 | 485 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 85 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01E5 | 486 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 86 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01E6 | 487 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 87 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01E7 | 488 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 88 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01E8 | 489 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 89 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01E9 | 490 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 90 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01EA | 491 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 91 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01EB | 492 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 92 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01EC | 493 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 93 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01ED | 494 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 94 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01EE | 495 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 95 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01EF | 496 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 96 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01F0 | 497 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 97 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01F1 | 498 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 98 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01F2 | 499 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 99 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01F3 | 500 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Product Identifier of the wireless device 100 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x01F6 | 503 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 1. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0200 | 513 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 2. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x020A | 523 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 3. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0214 | 533 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 4. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x021E | 543 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 5. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0228 | 553 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 6. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0232 | 563 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 7. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x023C | 573 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 8. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0246 | 583 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 9. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0250 | 593 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 10. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x025A | 603 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 11. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0264 | 613 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 12. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x026E | 623 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 13. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0278 | 633 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 14. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0282 | 643 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 15. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x028C | 653 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 16. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0296 | 663 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 17. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x02A0 | 673 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 18. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x02AA | 683 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 19. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x02B4 | 693 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 20. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x02BE | 703 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 21. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x02C8 | 713 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 22. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x02D2 | 723 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 23. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x02DC | 733 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 24. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x02E6 | 743 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 25. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x02F0 | 753 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 26. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x02FA | 763 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 27. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0304 | 773 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 28. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x030E | 783 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 29. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0318 | 793 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 30. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0322 | 803 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 31. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x032C | 813 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 32. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0336 | 823 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 33. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0340 | 833 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 34. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x034A | 843 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 35. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0354 | 853 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 36. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x035E | 863 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 37. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0368 | 873 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 38. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0372 | 883 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 39. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x037C | 893 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 40. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0386 | 903 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 41. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0390 | 913 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 42. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x039A | 923 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 43. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x03A4 | 933 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 44. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x03AE | 943 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 45. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x03B8 | 953 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 46. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x03C2 | 963 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 47. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x03CC | 973 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 48. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x03D6 | 983 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 49. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x03E0 | 993 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 50. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x03EA | 1003 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 51. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x03F4 | 1013 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 52. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x03FE | 1023 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 53. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0408 | 1033 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 54. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0412 | 1043 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 55. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x041C | 1053 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 56. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0426 | 1063 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 57. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0430 | 1073 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 58. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x043A | 1083 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 59. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0444 | 1093 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 60. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x044E | 1103 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 61. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0458 | 1113 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 62. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0462 | 1123 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 63. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x046C | 1133 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 64. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0476 | 1143 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 65. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0480 | 1153 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 66. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x048A | 1163 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 67. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0494 | 1173 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 68. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x049E | 1183 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 69. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x04A8 | 1193 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 70. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x04B2 | 1203 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 71. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x04BC | 1213 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 72. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x04C6 | 1223 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 73. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x04D0 | 1233 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 74. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x04DA | 1243 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 75. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x04E4 | 1253 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 76. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x04EE | 1263 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 77. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x04F8 | 1273 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 78. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0502 | 1283 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 79. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x050C | 1293 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 80. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0516 | 1303 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 81. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0520 | 1313 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 82. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x052A | 1323 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 83. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0534 | 1333 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 84. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x053E | 1343 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 85. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0548 | 1353 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 86. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0552 | 1363 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 87. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x055C | 1373 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 88. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0566 | 1383 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 89. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0570 | 1393 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 90. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x057A | 1403 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 91. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0584 | 1413 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 92. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x058E | 1423 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 93. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x0598 | 1433 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 94. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x05A2 | 1443 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 95. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x05AC | 1453 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 96. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x05B6 | 1463 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 97. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x05C0 | 1473 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 98. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x05CA | 1483 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 99. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Device Identification | 0x05D4 | 1493 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Device name of the wireless device 100. Only the first 20 characters are considered. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Configuration | 0x1388 | 5001 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 1 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x1389 | 5002 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 2 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x138A | 5003 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 3 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x138B | 5004 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 4 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x138C | 5005 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 5 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x138D | 5006 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 6 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x138E | 5007 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 7 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x138F | 5008 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 8 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x1390 | 5009 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 9 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x1391 | 5010 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 10 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x1392 | 5011 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 11 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x1393 | 5012 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 12 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x1394 | 5013 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 13 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x1395 | 5014 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 14 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x1396 | 5015 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 15 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x1397 | 5016 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 16 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x1398 | 5017 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 17 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x1399 | 5018 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 18 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x139A | 5019 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 19 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x139B | 5020 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 20 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x139C | 5021 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 21 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x139D | 5022 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 22 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x139E | 5023 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 23 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x139F | 5024 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 24 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13A0 | 5025 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 25 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13A1 | 5026 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 26 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13A2 | 5027 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 27 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13A3 | 5028 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 28 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13A4 | 5029 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 29 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13A5 | 5030 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 30 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13A6 | 5031 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 31 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13A7 | 5032 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 32 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13A8 | 5033 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 33 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13A9 | 5034 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 34 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13AA | 5035 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 35 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13AB | 5036 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 36 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13AC | 5037 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 37 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13AD | 5038 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 38 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13AE | 5039 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 39 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13AF | 5040 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 40 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13B0 | 5041 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 41 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13B1 | 5042 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 42 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13B2 | 5043 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 43 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13B3 | 5044 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 44 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13B4 | 5045 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 45 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13B5 | 5046 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 46 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13B6 | 5047 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 47 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13B7 | 5048 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 48 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13B8 | 5049 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 49 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13B9 | 5050 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 50 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13BA | 5051 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 51 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13BB | 5052 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 52 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13BC | 5053 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 53 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13BD | 5054 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 54 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13BE | 5055 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 55 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13BF | 5056 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 56 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13C0 | 5057 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 57 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13C1 | 5058 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 58 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13C2 | 5059 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 59 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13C3 | 5060 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 60 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13C4 | 5061 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 61 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13C5 | 5062 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 62 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13C6 | 5063 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 63 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13C7 | 5064 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 64 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13C8 | 5065 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 65 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13C9 | 5066 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 66 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13CA | 5067 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 67 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13CB | 5068 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 68 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13CC | 5069 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 69 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13CD | 5070 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 70 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13CE | 5071 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 71 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13CF | 5072 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 72 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13D0 | 5073 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 73 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13D1 | 5074 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 74 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13D2 | 5075 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 75 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13D3 | 5076 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 76 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13D4 | 5077 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 77 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13D5 | 5078 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 78 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13D6 | 5079 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 79 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13D7 | 5080 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 80 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13D8 | 5081 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 81 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13D9 | 5082 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 82 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13DA | 5083 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 83 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13DB | 5084 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 84 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13DC | 5085 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 85 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13DD | 5086 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 86 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13DE | 5087 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 87 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13DF | 5088 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 88 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13E0 | 5089 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 89 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13E1 | 5090 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 90 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13E2 | 5091 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 91 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13E3 | 5092 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 92 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13E4 | 5093 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 93 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13E5 | 5094 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 94 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13E6 | 5095 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 95 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13E7 | 5096 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 96 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13E8 | 5097 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 97 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13E9 | 5098 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 98 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13EA | 5099 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 99 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Configuration | 0x13EB | 5100 | 1 | R | - | A | UINT16 |  | 0xFFFF | N | 3, 100-4 | Rated current of the protective device to the wireless device 100 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Power Factor Metering Data | 0x13EC | 5101 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 1 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x13ED | 5102 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 2 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x13EE | 5103 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 3 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x13EF | 5104 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 4 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x13F0 | 5105 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 5 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x13F1 | 5106 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 6 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x13F2 | 5107 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 7 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x13F3 | 5108 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 8 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x13F4 | 5109 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 9 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x13F5 | 5110 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 10 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x13F6 | 5111 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 11 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x13F7 | 5112 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 12 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x13F8 | 5113 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 13 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x13F9 | 5114 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 14 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x13FA | 5115 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 15 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x13FB | 5116 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 16 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x13FC | 5117 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 17 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x13FD | 5118 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 18 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x13FE | 5119 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 19 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x13FF | 5120 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 20 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1400 | 5121 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 21 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1401 | 5122 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 22 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1402 | 5123 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 23 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1403 | 5124 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 24 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1404 | 5125 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 25 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1405 | 5126 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 26 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1406 | 5127 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 27 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1407 | 5128 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 28 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1408 | 5129 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 29 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1409 | 5130 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 30 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x140A | 5131 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 31 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x140B | 5132 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 32 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x140C | 5133 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 33 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x140D | 5134 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 34 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x140E | 5135 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 35 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x140F | 5136 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 36 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1410 | 5137 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 37 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1411 | 5138 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 38 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1412 | 5139 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 39 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1413 | 5140 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 40 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1414 | 5141 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 41 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1415 | 5142 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 42 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1416 | 5143 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 43 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1417 | 5144 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 44 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1418 | 5145 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 45 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1419 | 5146 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 46 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x141A | 5147 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 47 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x141B | 5148 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 48 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x141C | 5149 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 49 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x141D | 5150 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 50 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x141E | 5151 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 51 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x141F | 5152 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 52 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1420 | 5153 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 53 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1421 | 5154 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 54 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1422 | 5155 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 55 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1423 | 5156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 56 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1424 | 5157 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 57 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1425 | 5158 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 58 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1426 | 5159 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 59 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1427 | 5160 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 60 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1428 | 5161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 61 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1429 | 5162 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 62 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x142A | 5163 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 63 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x142B | 5164 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 64 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x142C | 5165 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 65 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x142D | 5166 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 66 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x142E | 5167 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 67 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x142F | 5168 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 68 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1430 | 5169 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 69 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1431 | 5170 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 70 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1432 | 5171 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 71 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1433 | 5172 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 72 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1434 | 5173 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 73 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1435 | 5174 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 74 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1436 | 5175 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 75 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1437 | 5176 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 76 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1438 | 5177 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 77 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1439 | 5178 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 78 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x143A | 5179 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 79 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x143B | 5180 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 80 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x143C | 5181 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 81 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x143D | 5182 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 82 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x143E | 5183 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 83 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x143F | 5184 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 84 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1440 | 5185 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 85 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1441 | 5186 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 86 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1442 | 5187 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 87 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1443 | 5188 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 88 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1444 | 5189 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 89 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1445 | 5190 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 90 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1446 | 5191 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 91 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1447 | 5192 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 92 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1448 | 5193 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 93 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x1449 | 5194 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 94 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x144A | 5195 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 95 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x144B | 5196 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 96 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x144C | 5197 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 97 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x144D | 5198 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 98 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x144E | 5199 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 99 |  | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x144F | 5200 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | PowerFactor sign convention of the wireless device 100 |  | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1770 | 6001 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 1 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1772 | 6003 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 2 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1774 | 6005 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 3 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1776 | 6007 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 4 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1778 | 6009 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 5 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x177A | 6011 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 6 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x177C | 6013 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 7 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x177E | 6015 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 8 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1780 | 6017 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 9 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1782 | 6019 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 10 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1784 | 6021 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 11 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1786 | 6023 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 12 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1788 | 6025 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 13 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x178A | 6027 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 14 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x178C | 6029 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 15 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x178E | 6031 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 16 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1790 | 6033 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 17 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1792 | 6035 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 18 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1794 | 6037 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 19 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1796 | 6039 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 20 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1798 | 6041 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 21 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x179A | 6043 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 22 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x179C | 6045 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 23 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x179E | 6047 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 24 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17A0 | 6049 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 25 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17A2 | 6051 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 26 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17A4 | 6053 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 27 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17A6 | 6055 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 28 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17A8 | 6057 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 29 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17AA | 6059 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 30 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17AC | 6061 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 31 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17AE | 6063 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 32 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17B0 | 6065 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 33 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17B2 | 6067 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 34 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17B4 | 6069 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 35 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17B6 | 6071 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 36 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17B8 | 6073 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 37 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17BA | 6075 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 38 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17BC | 6077 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 39 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17BE | 6079 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 40 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17C0 | 6081 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 41 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17C2 | 6083 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 42 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17C4 | 6085 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 43 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17C6 | 6087 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 44 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17C8 | 6089 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 45 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17CA | 6091 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 46 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17CC | 6093 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 47 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17CE | 6095 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 48 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17D0 | 6097 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 49 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17D2 | 6099 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 50 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17D4 | 6101 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 51 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17D6 | 6103 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 52 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17D8 | 6105 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 53 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17DA | 6107 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 54 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17DC | 6109 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 55 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17DE | 6111 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 56 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17E0 | 6113 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 57 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17E2 | 6115 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 58 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17E4 | 6117 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 59 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17E6 | 6119 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 60 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17E8 | 6121 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 61 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17EA | 6123 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 62 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17EC | 6125 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 63 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17EE | 6127 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 64 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17F0 | 6129 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 65 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17F2 | 6131 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 66 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17F4 | 6133 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 67 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17F6 | 6135 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 68 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17F8 | 6137 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 69 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17FA | 6139 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 70 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17FC | 6141 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 71 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x17FE | 6143 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 72 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1800 | 6145 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 73 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1802 | 6147 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 74 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1804 | 6149 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 75 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1806 | 6151 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 76 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1808 | 6153 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 77 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x180A | 6155 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 78 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x180C | 6157 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 79 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x180E | 6159 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 80 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1810 | 6161 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 81 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1812 | 6163 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 82 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1814 | 6165 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 83 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1816 | 6167 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 84 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1818 | 6169 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 85 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x181A | 6171 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 86 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x181C | 6173 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 87 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x181E | 6175 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 88 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1820 | 6177 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 89 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1822 | 6179 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 90 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1824 | 6181 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 91 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1826 | 6183 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 92 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1828 | 6185 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 93 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x182A | 6187 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 94 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x182C | 6189 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 95 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x182E | 6191 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 96 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1830 | 6193 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 97 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1832 | 6195 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 98 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1834 | 6197 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 99 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1836 | 6199 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power of wireless device 100 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1838 | 6201 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 1 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x183A | 6203 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 2 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x183C | 6205 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 3 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x183E | 6207 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 4 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1840 | 6209 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 5 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1842 | 6211 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 6 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1844 | 6213 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 7 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1846 | 6215 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 8 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1848 | 6217 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 9 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x184A | 6219 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 10 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x184C | 6221 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 11 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x184E | 6223 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 12 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1850 | 6225 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 13 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1852 | 6227 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 14 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1854 | 6229 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 15 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1856 | 6231 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 16 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1858 | 6233 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 17 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x185A | 6235 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 18 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x185C | 6237 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 19 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x185E | 6239 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 20 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1860 | 6241 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 21 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1862 | 6243 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 22 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1864 | 6245 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 23 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1866 | 6247 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 24 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1868 | 6249 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 25 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x186A | 6251 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 26 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x186C | 6253 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 27 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x186E | 6255 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 28 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1870 | 6257 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 29 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1872 | 6259 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 30 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1874 | 6261 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 31 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1876 | 6263 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 32 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1878 | 6265 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 33 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x187A | 6267 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 34 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x187C | 6269 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 35 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x187E | 6271 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 36 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1880 | 6273 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 37 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1882 | 6275 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 38 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1884 | 6277 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 39 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1886 | 6279 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 40 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1888 | 6281 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 41 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x188A | 6283 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 42 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x188C | 6285 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 43 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x188E | 6287 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 44 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1890 | 6289 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 45 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1892 | 6291 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 46 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1894 | 6293 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 47 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1896 | 6295 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 48 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1898 | 6297 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 49 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x189A | 6299 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 50 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x189C | 6301 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 51 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x189E | 6303 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 52 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18A0 | 6305 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 53 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18A2 | 6307 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 54 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18A4 | 6309 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 55 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18A6 | 6311 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 56 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18A8 | 6313 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 57 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18AA | 6315 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 58 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18AC | 6317 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 59 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18AE | 6319 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 60 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18B0 | 6321 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 61 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18B2 | 6323 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 62 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18B4 | 6325 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 63 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18B6 | 6327 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 64 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18B8 | 6329 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 65 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18BA | 6331 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 66 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18BC | 6333 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 67 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18BE | 6335 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 68 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18C0 | 6337 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 69 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18C2 | 6339 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 70 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18C4 | 6341 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 71 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18C6 | 6343 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 72 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18C8 | 6345 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 73 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18CA | 6347 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 74 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18CC | 6349 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 75 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18CE | 6351 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 76 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18D0 | 6353 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 77 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18D2 | 6355 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 78 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18D4 | 6357 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 79 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18D6 | 6359 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 80 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18D8 | 6361 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 81 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18DA | 6363 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 82 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18DC | 6365 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 83 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18DE | 6367 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 84 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18E0 | 6369 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 85 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18E2 | 6371 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 86 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18E4 | 6373 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 87 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18E6 | 6375 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 88 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18E8 | 6377 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 89 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18EA | 6379 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 90 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18EC | 6381 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 91 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18EE | 6383 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 92 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18F0 | 6385 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 93 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18F2 | 6387 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 94 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18F4 | 6389 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 95 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18F6 | 6391 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 96 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18F8 | 6393 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 97 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18FA | 6395 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 98 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18FC | 6397 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 99 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x18FE | 6399 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Peak demand total active power of wireless device 100 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1900 | 6401 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 1 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1904 | 6405 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 2 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1908 | 6409 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 3 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x190C | 6413 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 4 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1910 | 6417 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 5 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1914 | 6421 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 6 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1918 | 6425 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 7 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x191C | 6429 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 8 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1920 | 6433 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 9 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1924 | 6437 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 10 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1928 | 6441 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 11 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x192C | 6445 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 12 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1930 | 6449 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 13 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1934 | 6453 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 14 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1938 | 6457 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 15 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x193C | 6461 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 16 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1940 | 6465 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 17 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1944 | 6469 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 18 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1948 | 6473 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 19 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x194C | 6477 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 20 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1950 | 6481 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 21 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1954 | 6485 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 22 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1958 | 6489 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 23 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x195C | 6493 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 24 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1960 | 6497 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 25 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1964 | 6501 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 26 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1968 | 6505 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 27 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x196C | 6509 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 28 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1970 | 6513 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 29 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1974 | 6517 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 30 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1978 | 6521 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 31 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x197C | 6525 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 32 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1980 | 6529 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 33 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1984 | 6533 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 34 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1988 | 6537 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 35 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x198C | 6541 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 36 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1990 | 6545 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 37 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1994 | 6549 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 38 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1998 | 6553 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 39 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x199C | 6557 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 40 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x19A0 | 6561 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 41 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x19A4 | 6565 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 42 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x19A8 | 6569 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 43 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x19AC | 6573 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 44 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x19B0 | 6577 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 45 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x19B4 | 6581 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 46 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x19B8 | 6585 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 47 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x19BC | 6589 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 48 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x19C0 | 6593 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 49 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x19C4 | 6597 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 50 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x19C8 | 6601 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 51 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x19CC | 6605 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 52 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x19D0 | 6609 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 53 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x19D4 | 6613 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 54 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x19D8 | 6617 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 55 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x19DC | 6621 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 56 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x19E0 | 6625 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 57 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x19E4 | 6629 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 58 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x19E8 | 6633 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 59 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x19EC | 6637 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 60 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x19F0 | 6641 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 61 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x19F4 | 6645 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 62 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x19F8 | 6649 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 63 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x19FC | 6653 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 64 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A00 | 6657 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 65 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A04 | 6661 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 66 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A08 | 6665 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 67 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A0C | 6669 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 68 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A10 | 6673 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 69 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A14 | 6677 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 70 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A18 | 6681 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 71 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A1C | 6685 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 72 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A20 | 6689 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 73 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A24 | 6693 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 74 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A28 | 6697 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 75 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A2C | 6701 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 76 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A30 | 6705 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 77 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A34 | 6709 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 78 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A38 | 6713 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 79 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A3C | 6717 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 80 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A40 | 6721 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 81 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A44 | 6725 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 82 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A48 | 6729 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 83 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A4C | 6733 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 84 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A50 | 6737 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 85 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A54 | 6741 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 86 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A58 | 6745 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 87 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A5C | 6749 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 88 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A60 | 6753 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 89 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A64 | 6757 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 90 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A68 | 6761 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 91 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A6C | 6765 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 92 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A70 | 6769 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 93 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A74 | 6773 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 94 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A78 | 6777 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 95 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A7C | 6781 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 96 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A80 | 6785 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 97 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A84 | 6789 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 98 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A88 | 6793 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 99 | x | x | x | [5 empty] | x | [5 empty] | x
Power Demand Data | 0x1A8C | 6797 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4 | Peak demand total active power timestamp of wireless device 100 | x | x | x | [5 empty] | x | [5 empty] | x
Current Metering Data | 0x1A90 | 6801 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 1 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1A92 | 6803 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 2 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1A94 | 6805 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 3 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1A96 | 6807 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 4 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1A98 | 6809 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 5 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1A9A | 6811 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 6 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1A9C | 6813 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 7 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1A9E | 6815 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 8 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AA0 | 6817 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 9 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AA2 | 6819 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 10 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AA4 | 6821 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 11 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AA6 | 6823 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 12 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AA8 | 6825 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 13 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AAA | 6827 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 14 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AAC | 6829 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 15 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AAE | 6831 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 16 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AB0 | 6833 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 17 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AB2 | 6835 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 18 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AB4 | 6837 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 19 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AB6 | 6839 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 20 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AB8 | 6841 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 21 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1ABA | 6843 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 22 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1ABC | 6845 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 23 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1ABE | 6847 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 24 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AC0 | 6849 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 25 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AC2 | 6851 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 26 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AC4 | 6853 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 27 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AC6 | 6855 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 28 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AC8 | 6857 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 29 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1ACA | 6859 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 30 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1ACC | 6861 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 31 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1ACE | 6863 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 32 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AD0 | 6865 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 33 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AD2 | 6867 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 34 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AD4 | 6869 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 35 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AD6 | 6871 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 36 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AD8 | 6873 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 37 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1ADA | 6875 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 38 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1ADC | 6877 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 39 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1ADE | 6879 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 40 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AE0 | 6881 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 41 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AE2 | 6883 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 42 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AE4 | 6885 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 43 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AE6 | 6887 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 44 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AE8 | 6889 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 45 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AEA | 6891 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 46 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AEC | 6893 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 47 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AEE | 6895 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 48 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AF0 | 6897 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 49 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AF2 | 6899 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 50 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AF4 | 6901 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 51 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AF6 | 6903 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 52 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AF8 | 6905 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 53 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AFA | 6907 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 54 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AFC | 6909 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 55 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1AFE | 6911 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 56 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B00 | 6913 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 57 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B02 | 6915 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 58 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B04 | 6917 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 59 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B06 | 6919 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 60 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B08 | 6921 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 61 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B0A | 6923 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 62 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B0C | 6925 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 63 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B0E | 6927 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 64 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B10 | 6929 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 65 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B12 | 6931 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 66 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B14 | 6933 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 67 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B16 | 6935 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 68 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B18 | 6937 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 69 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B1A | 6939 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 70 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B1C | 6941 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 71 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B1E | 6943 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 72 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B20 | 6945 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 73 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B22 | 6947 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 74 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B24 | 6949 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 75 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B26 | 6951 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 76 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B28 | 6953 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 77 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B2A | 6955 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 78 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B2C | 6957 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 79 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B2E | 6959 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 80 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B30 | 6961 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 81 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B32 | 6963 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 82 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B34 | 6965 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 83 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B36 | 6967 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 84 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B38 | 6969 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 85 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B3A | 6971 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 86 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B3C | 6973 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 87 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B3E | 6975 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 88 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B40 | 6977 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 89 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B42 | 6979 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 90 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B44 | 6981 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 91 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B46 | 6983 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 92 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B48 | 6985 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 93 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B4A | 6987 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 94 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B4C | 6989 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 95 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B4E | 6991 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 96 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B50 | 6993 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 97 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B52 | 6995 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 98 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B54 | 6997 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 99 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B56 | 6999 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A of wireless device 100 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B58 | 7001 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 1 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B5A | 7003 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 2 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B5C | 7005 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 3 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B5E | 7007 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 4 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B60 | 7009 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 5 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B62 | 7011 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 6 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B64 | 7013 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 7 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B66 | 7015 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 8 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B68 | 7017 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 9 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B6A | 7019 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 10 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B6C | 7021 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 11 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B6E | 7023 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 12 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B70 | 7025 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 13 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B72 | 7027 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 14 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B74 | 7029 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 15 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B76 | 7031 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 16 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B78 | 7033 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 17 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B7A | 7035 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 18 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B7C | 7037 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 19 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B7E | 7039 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 20 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B80 | 7041 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 21 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B82 | 7043 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 22 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B84 | 7045 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 23 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B86 | 7047 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 24 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B88 | 7049 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 25 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B8A | 7051 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 26 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B8C | 7053 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 27 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B8E | 7055 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 28 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B90 | 7057 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 29 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B92 | 7059 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 30 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B94 | 7061 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 31 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B96 | 7063 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 32 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B98 | 7065 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 33 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B9A | 7067 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 34 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B9C | 7069 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 35 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1B9E | 7071 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 36 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BA0 | 7073 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 37 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BA2 | 7075 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 38 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BA4 | 7077 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 39 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BA6 | 7079 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 40 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BA8 | 7081 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 41 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BAA | 7083 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 42 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BAC | 7085 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 43 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BAE | 7087 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 44 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BB0 | 7089 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 45 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BB2 | 7091 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 46 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BB4 | 7093 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 47 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BB6 | 7095 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 48 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BB8 | 7097 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 49 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BBA | 7099 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 50 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BBC | 7101 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 51 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BBE | 7103 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 52 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BC0 | 7105 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 53 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BC2 | 7107 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 54 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BC4 | 7109 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 55 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BC6 | 7111 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 56 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BC8 | 7113 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 57 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BCA | 7115 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 58 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BCC | 7117 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 59 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BCE | 7119 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 60 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BD0 | 7121 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 61 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BD2 | 7123 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 62 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BD4 | 7125 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 63 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BD6 | 7127 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 64 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BD8 | 7129 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 65 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BDA | 7131 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 66 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BDC | 7133 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 67 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BDE | 7135 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 68 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BE0 | 7137 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 69 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BE2 | 7139 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 70 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BE4 | 7141 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 71 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BE6 | 7143 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 72 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BE8 | 7145 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 73 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BEA | 7147 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 74 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BEC | 7149 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 75 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BEE | 7151 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 76 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BF0 | 7153 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 77 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BF2 | 7155 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 78 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BF4 | 7157 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 79 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BF6 | 7159 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 80 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BF8 | 7161 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 81 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BFA | 7163 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 82 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BFC | 7165 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 83 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1BFE | 7167 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 84 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C00 | 7169 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 85 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C02 | 7171 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 86 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C04 | 7173 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 87 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C06 | 7175 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 88 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C08 | 7177 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 89 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C0A | 7179 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 90 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C0C | 7181 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 91 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C0E | 7183 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 92 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C10 | 7185 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 93 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C12 | 7187 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 94 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C14 | 7189 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 95 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C16 | 7191 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 96 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C18 | 7193 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 97 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C1A | 7195 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 98 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C1C | 7197 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 99 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C1E | 7199 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B of wireless device 100 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C20 | 7201 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 1 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C22 | 7203 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 2 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C24 | 7205 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 3 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C26 | 7207 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 4 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C28 | 7209 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 5 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C2A | 7211 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 6 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C2C | 7213 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 7 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C2E | 7215 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 8 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C30 | 7217 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 9 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C32 | 7219 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 10 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C34 | 7221 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 11 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C36 | 7223 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 12 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C38 | 7225 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 13 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C3A | 7227 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 14 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C3C | 7229 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 15 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C3E | 7231 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 16 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C40 | 7233 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 17 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C42 | 7235 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 18 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C44 | 7237 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 19 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C46 | 7239 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 20 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C48 | 7241 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 21 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C4A | 7243 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 22 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C4C | 7245 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 23 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C4E | 7247 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 24 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C50 | 7249 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 25 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C52 | 7251 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 26 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C54 | 7253 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 27 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C56 | 7255 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 28 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C58 | 7257 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 29 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C5A | 7259 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 30 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C5C | 7261 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 31 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C5E | 7263 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 32 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C60 | 7265 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 33 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C62 | 7267 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 34 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C64 | 7269 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 35 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C66 | 7271 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 36 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C68 | 7273 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 37 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C6A | 7275 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 38 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C6C | 7277 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 39 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C6E | 7279 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 40 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C70 | 7281 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 41 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C72 | 7283 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 42 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C74 | 7285 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 43 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C76 | 7287 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 44 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C78 | 7289 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 45 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C7A | 7291 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 46 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C7C | 7293 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 47 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C7E | 7295 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 48 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C80 | 7297 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 49 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C82 | 7299 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 50 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C84 | 7301 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 51 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C86 | 7303 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 52 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C88 | 7305 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 53 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C8A | 7307 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 54 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C8C | 7309 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 55 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C8E | 7311 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 56 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C90 | 7313 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 57 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C92 | 7315 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 58 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C94 | 7317 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 59 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C96 | 7319 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 60 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C98 | 7321 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 61 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C9A | 7323 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 62 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C9C | 7325 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 63 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1C9E | 7327 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 64 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CA0 | 7329 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 65 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CA2 | 7331 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 66 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CA4 | 7333 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 67 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CA6 | 7335 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 68 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CA8 | 7337 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 69 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CAA | 7339 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 70 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CAC | 7341 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 71 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CAE | 7343 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 72 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CB0 | 7345 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 73 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CB2 | 7347 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 74 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CB4 | 7349 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 75 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CB6 | 7351 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 76 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CB8 | 7353 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 77 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CBA | 7355 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 78 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CBC | 7357 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 79 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CBE | 7359 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 80 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CC0 | 7361 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 81 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CC2 | 7363 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 82 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CC4 | 7365 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 83 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CC6 | 7367 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 84 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CC8 | 7369 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 85 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CCA | 7371 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 86 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CCC | 7373 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 87 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CCE | 7375 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 88 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CD0 | 7377 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 89 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CD2 | 7379 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 90 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CD4 | 7381 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 91 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CD6 | 7383 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 92 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CD8 | 7385 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 93 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CDA | 7387 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 94 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CDC | 7389 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 95 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CDE | 7391 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 96 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CE0 | 7393 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 97 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CE2 | 7395 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 98 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CE4 | 7397 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 99 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CE6 | 7399 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C of wireless device 100 | x | x | x | [5 empty] | x |  |  |  |  | x | x
Current Metering Data | 0x1CE8 | 7401 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 1 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1CEA | 7403 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 2 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1CEC | 7405 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 3 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1CEE | 7407 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 4 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1CF0 | 7409 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 5 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1CF2 | 7411 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 6 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1CF4 | 7413 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 7 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1CF6 | 7415 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 8 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1CF8 | 7417 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 9 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1CFA | 7419 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 10 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1CFC | 7421 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 11 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1CFE | 7423 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 12 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D00 | 7425 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 13 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D02 | 7427 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 14 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D04 | 7429 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 15 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D06 | 7431 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 16 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D08 | 7433 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 17 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D0A | 7435 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 18 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D0C | 7437 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 19 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D0E | 7439 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 20 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D10 | 7441 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 21 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D12 | 7443 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 22 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D14 | 7445 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 23 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D16 | 7447 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 24 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D18 | 7449 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 25 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D1A | 7451 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 26 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D1C | 7453 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 27 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D1E | 7455 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 28 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D20 | 7457 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 29 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D22 | 7459 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 30 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D24 | 7461 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 31 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D26 | 7463 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 32 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D28 | 7465 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 33 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D2A | 7467 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 34 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D2C | 7469 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 35 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D2E | 7471 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 36 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D30 | 7473 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 37 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D32 | 7475 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 38 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D34 | 7477 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 39 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D36 | 7479 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 40 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D38 | 7481 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 41 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D3A | 7483 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 42 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D3C | 7485 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 43 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D3E | 7487 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 44 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D40 | 7489 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 45 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D42 | 7491 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 46 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D44 | 7493 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 47 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D46 | 7495 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 48 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D48 | 7497 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 49 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D4A | 7499 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 50 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D4C | 7501 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 51 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D4E | 7503 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 52 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D50 | 7505 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 53 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D52 | 7507 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 54 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D54 | 7509 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 55 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D56 | 7511 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 56 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D58 | 7513 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 57 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D5A | 7515 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 58 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D5C | 7517 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 59 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D5E | 7519 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 60 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D60 | 7521 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 61 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D62 | 7523 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 62 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D64 | 7525 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 63 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D66 | 7527 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 64 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D68 | 7529 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 65 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D6A | 7531 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 66 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D6C | 7533 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 67 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D6E | 7535 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 68 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D70 | 7537 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 69 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D72 | 7539 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 70 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D74 | 7541 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 71 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D76 | 7543 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 72 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D78 | 7545 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 73 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D7A | 7547 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 74 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D7C | 7549 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 75 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D7E | 7551 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 76 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D80 | 7553 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 77 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D82 | 7555 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 78 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D84 | 7557 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 79 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D86 | 7559 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 80 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D88 | 7561 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 81 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D8A | 7563 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 82 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D8C | 7565 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 83 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D8E | 7567 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 84 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D90 | 7569 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 85 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D92 | 7571 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 86 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D94 | 7573 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 87 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D96 | 7575 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 88 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D98 | 7577 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 89 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D9A | 7579 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 90 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D9C | 7581 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 91 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1D9E | 7583 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 92 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1DA0 | 7585 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 93 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1DA2 | 7587 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 94 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1DA4 | 7589 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 95 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1DA6 | 7591 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 96 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1DA8 | 7593 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 97 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1DAA | 7595 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 98 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1DAC | 7597 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 99 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1DAE | 7599 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral of wireless device 100 |  |  | x | [10 empty] | x | x
Current Metering Data | 0x1DB0 | 7601 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 1 | [14 empty] | x
Current Metering Data | 0x1DB2 | 7603 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 2 | [14 empty] | x
Current Metering Data | 0x1DB4 | 7605 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 3 | [14 empty] | x
Current Metering Data | 0x1DB6 | 7607 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 4 | [14 empty] | x
Current Metering Data | 0x1DB8 | 7609 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 5 | [14 empty] | x
Current Metering Data | 0x1DBA | 7611 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 6 | [14 empty] | x
Current Metering Data | 0x1DBC | 7613 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 7 | [14 empty] | x
Current Metering Data | 0x1DBE | 7615 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 8 | [14 empty] | x
Current Metering Data | 0x1DC0 | 7617 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 9 | [14 empty] | x
Current Metering Data | 0x1DC2 | 7619 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 10 | [14 empty] | x
Current Metering Data | 0x1DC4 | 7621 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 11 | [14 empty] | x
Current Metering Data | 0x1DC6 | 7623 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 12 | [14 empty] | x
Current Metering Data | 0x1DC8 | 7625 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 13 | [14 empty] | x
Current Metering Data | 0x1DCA | 7627 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 14 | [14 empty] | x
Current Metering Data | 0x1DCC | 7629 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 15 | [14 empty] | x
Current Metering Data | 0x1DCE | 7631 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 16 | [14 empty] | x
Current Metering Data | 0x1DD0 | 7633 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 17 | [14 empty] | x
Current Metering Data | 0x1DD2 | 7635 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 18 | [14 empty] | x
Current Metering Data | 0x1DD4 | 7637 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 19 | [14 empty] | x
Current Metering Data | 0x1DD6 | 7639 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 20 | [14 empty] | x
Current Metering Data | 0x1DD8 | 7641 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 21 | [14 empty] | x
Current Metering Data | 0x1DDA | 7643 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 22 | [14 empty] | x
Current Metering Data | 0x1DDC | 7645 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 23 | [14 empty] | x
Current Metering Data | 0x1DDE | 7647 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 24 | [14 empty] | x
Current Metering Data | 0x1DE0 | 7649 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 25 | [14 empty] | x
Current Metering Data | 0x1DE2 | 7651 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 26 | [14 empty] | x
Current Metering Data | 0x1DE4 | 7653 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 27 | [14 empty] | x
Current Metering Data | 0x1DE6 | 7655 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 28 | [14 empty] | x
Current Metering Data | 0x1DE8 | 7657 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 29 | [14 empty] | x
Current Metering Data | 0x1DEA | 7659 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 30 | [14 empty] | x
Current Metering Data | 0x1DEC | 7661 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 31 | [14 empty] | x
Current Metering Data | 0x1DEE | 7663 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 32 | [14 empty] | x
Current Metering Data | 0x1DF0 | 7665 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 33 | [14 empty] | x
Current Metering Data | 0x1DF2 | 7667 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 34 | [14 empty] | x
Current Metering Data | 0x1DF4 | 7669 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 35 | [14 empty] | x
Current Metering Data | 0x1DF6 | 7671 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 36 | [14 empty] | x
Current Metering Data | 0x1DF8 | 7673 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 37 | [14 empty] | x
Current Metering Data | 0x1DFA | 7675 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 38 | [14 empty] | x
Current Metering Data | 0x1DFC | 7677 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 39 | [14 empty] | x
Current Metering Data | 0x1DFE | 7679 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 40 | [14 empty] | x
Current Metering Data | 0x1E00 | 7681 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 41 | [14 empty] | x
Current Metering Data | 0x1E02 | 7683 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 42 | [14 empty] | x
Current Metering Data | 0x1E04 | 7685 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 43 | [14 empty] | x
Current Metering Data | 0x1E06 | 7687 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 44 | [14 empty] | x
Current Metering Data | 0x1E08 | 7689 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 45 | [14 empty] | x
Current Metering Data | 0x1E0A | 7691 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 46 | [14 empty] | x
Current Metering Data | 0x1E0C | 7693 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 47 | [14 empty] | x
Current Metering Data | 0x1E0E | 7695 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 48 | [14 empty] | x
Current Metering Data | 0x1E10 | 7697 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 49 | [14 empty] | x
Current Metering Data | 0x1E12 | 7699 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 50 | [14 empty] | x
Current Metering Data | 0x1E14 | 7701 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 51 | [14 empty] | x
Current Metering Data | 0x1E16 | 7703 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 52 | [14 empty] | x
Current Metering Data | 0x1E18 | 7705 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 53 | [14 empty] | x
Current Metering Data | 0x1E1A | 7707 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 54 | [14 empty] | x
Current Metering Data | 0x1E1C | 7709 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 55 | [14 empty] | x
Current Metering Data | 0x1E1E | 7711 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 56 | [14 empty] | x
Current Metering Data | 0x1E20 | 7713 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 57 | [14 empty] | x
Current Metering Data | 0x1E22 | 7715 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 58 | [14 empty] | x
Current Metering Data | 0x1E24 | 7717 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 59 | [14 empty] | x
Current Metering Data | 0x1E26 | 7719 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 60 | [14 empty] | x
Current Metering Data | 0x1E28 | 7721 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 61 | [14 empty] | x
Current Metering Data | 0x1E2A | 7723 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 62 | [14 empty] | x
Current Metering Data | 0x1E2C | 7725 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 63 | [14 empty] | x
Current Metering Data | 0x1E2E | 7727 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 64 | [14 empty] | x
Current Metering Data | 0x1E30 | 7729 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 65 | [14 empty] | x
Current Metering Data | 0x1E32 | 7731 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 66 | [14 empty] | x
Current Metering Data | 0x1E34 | 7733 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 67 | [14 empty] | x
Current Metering Data | 0x1E36 | 7735 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 68 | [14 empty] | x
Current Metering Data | 0x1E38 | 7737 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 69 | [14 empty] | x
Current Metering Data | 0x1E3A | 7739 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 70 | [14 empty] | x
Current Metering Data | 0x1E3C | 7741 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 71 | [14 empty] | x
Current Metering Data | 0x1E3E | 7743 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 72 | [14 empty] | x
Current Metering Data | 0x1E40 | 7745 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 73 | [14 empty] | x
Current Metering Data | 0x1E42 | 7747 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 74 | [14 empty] | x
Current Metering Data | 0x1E44 | 7749 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 75 | [14 empty] | x
Current Metering Data | 0x1E46 | 7751 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 76 | [14 empty] | x
Current Metering Data | 0x1E48 | 7753 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 77 | [14 empty] | x
Current Metering Data | 0x1E4A | 7755 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 78 | [14 empty] | x
Current Metering Data | 0x1E4C | 7757 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 79 | [14 empty] | x
Current Metering Data | 0x1E4E | 7759 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 80 | [14 empty] | x
Current Metering Data | 0x1E50 | 7761 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 81 | [14 empty] | x
Current Metering Data | 0x1E52 | 7763 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 82 | [14 empty] | x
Current Metering Data | 0x1E54 | 7765 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 83 | [14 empty] | x
Current Metering Data | 0x1E56 | 7767 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 84 | [14 empty] | x
Current Metering Data | 0x1E58 | 7769 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 85 | [14 empty] | x
Current Metering Data | 0x1E5A | 7771 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 86 | [14 empty] | x
Current Metering Data | 0x1E5C | 7773 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 87 | [14 empty] | x
Current Metering Data | 0x1E5E | 7775 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 88 | [14 empty] | x
Current Metering Data | 0x1E60 | 7777 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 89 | [14 empty] | x
Current Metering Data | 0x1E62 | 7779 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 90 | [14 empty] | x
Current Metering Data | 0x1E64 | 7781 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 91 | [14 empty] | x
Current Metering Data | 0x1E66 | 7783 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 92 | [14 empty] | x
Current Metering Data | 0x1E68 | 7785 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 93 | [14 empty] | x
Current Metering Data | 0x1E6A | 7787 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 94 | [14 empty] | x
Current Metering Data | 0x1E6C | 7789 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 95 | [14 empty] | x
Current Metering Data | 0x1E6E | 7791 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 96 | [14 empty] | x
Current Metering Data | 0x1E70 | 7793 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 97 | [14 empty] | x
Current Metering Data | 0x1E72 | 7795 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 98 | [14 empty] | x
Current Metering Data | 0x1E74 | 7797 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 99 | [14 empty] | x
Current Metering Data | 0x1E76 | 7799 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents of wireless device 100 | [14 empty] | x
Voltage Metering Data | 0x1E78 | 7801 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 1 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1E7A | 7803 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 2 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1E7C | 7805 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 3 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1E7E | 7807 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 4 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1E80 | 7809 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 5 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1E82 | 7811 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 6 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1E84 | 7813 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 7 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1E86 | 7815 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 8 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1E88 | 7817 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 9 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1E8A | 7819 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 10 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1E8C | 7821 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 11 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1E8E | 7823 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 12 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1E90 | 7825 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 13 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1E92 | 7827 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 14 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1E94 | 7829 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 15 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1E96 | 7831 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 16 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1E98 | 7833 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 17 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1E9A | 7835 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 18 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1E9C | 7837 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 19 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1E9E | 7839 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 20 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EA0 | 7841 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 21 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EA2 | 7843 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 22 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EA4 | 7845 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 23 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EA6 | 7847 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 24 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EA8 | 7849 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 25 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EAA | 7851 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 26 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EAC | 7853 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 27 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EAE | 7855 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 28 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EB0 | 7857 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 29 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EB2 | 7859 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 30 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EB4 | 7861 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 31 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EB6 | 7863 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 32 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EB8 | 7865 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 33 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EBA | 7867 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 34 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EBC | 7869 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 35 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EBE | 7871 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 36 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EC0 | 7873 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 37 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EC2 | 7875 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 38 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EC4 | 7877 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 39 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EC6 | 7879 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 40 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EC8 | 7881 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 41 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1ECA | 7883 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 42 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1ECC | 7885 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 43 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1ECE | 7887 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 44 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1ED0 | 7889 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 45 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1ED2 | 7891 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 46 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1ED4 | 7893 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 47 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1ED6 | 7895 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 48 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1ED8 | 7897 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 49 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EDA | 7899 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 50 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EDC | 7901 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 51 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EDE | 7903 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 52 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EE0 | 7905 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 53 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EE2 | 7907 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 54 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EE4 | 7909 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 55 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EE6 | 7911 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 56 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EE8 | 7913 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 57 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EEA | 7915 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 58 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EEC | 7917 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 59 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EEE | 7919 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 60 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EF0 | 7921 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 61 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EF2 | 7923 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 62 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EF4 | 7925 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 63 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EF6 | 7927 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 64 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EF8 | 7929 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 65 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EFA | 7931 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 66 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EFC | 7933 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 67 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1EFE | 7935 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 68 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F00 | 7937 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 69 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F02 | 7939 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 70 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F04 | 7941 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 71 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F06 | 7943 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 72 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F08 | 7945 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 73 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F0A | 7947 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 74 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F0C | 7949 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 75 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F0E | 7951 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 76 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F10 | 7953 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 77 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F12 | 7955 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 78 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F14 | 7957 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 79 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F16 | 7959 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 80 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F18 | 7961 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 81 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F1A | 7963 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 82 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F1C | 7965 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 83 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F1E | 7967 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 84 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F20 | 7969 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 85 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F22 | 7971 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 86 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F24 | 7973 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 87 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F26 | 7975 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 88 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F28 | 7977 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 89 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F2A | 7979 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 90 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F2C | 7981 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 91 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F2E | 7983 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 92 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F30 | 7985 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 93 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F32 | 7987 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 94 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F34 | 7989 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 95 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F36 | 7991 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 96 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F38 | 7993 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 97 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F3A | 7995 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 98 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F3C | 7997 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 99 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F3E | 7999 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B of wireless device 100 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F40 | 8001 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 1 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F42 | 8003 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 2 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F44 | 8005 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 3 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F46 | 8007 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 4 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F48 | 8009 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 5 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F4A | 8011 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 6 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F4C | 8013 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 7 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F4E | 8015 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 8 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F50 | 8017 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 9 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F52 | 8019 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 10 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F54 | 8021 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 11 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F56 | 8023 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 12 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F58 | 8025 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 13 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F5A | 8027 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 14 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F5C | 8029 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 15 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F5E | 8031 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 16 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F60 | 8033 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 17 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F62 | 8035 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 18 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F64 | 8037 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 19 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F66 | 8039 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 20 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F68 | 8041 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 21 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F6A | 8043 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 22 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F6C | 8045 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 23 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F6E | 8047 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 24 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F70 | 8049 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 25 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F72 | 8051 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 26 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F74 | 8053 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 27 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F76 | 8055 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 28 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F78 | 8057 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 29 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F7A | 8059 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 30 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F7C | 8061 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 31 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F7E | 8063 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 32 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F80 | 8065 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 33 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F82 | 8067 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 34 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F84 | 8069 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 35 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F86 | 8071 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 36 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F88 | 8073 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 37 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F8A | 8075 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 38 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F8C | 8077 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 39 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F8E | 8079 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 40 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F90 | 8081 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 41 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F92 | 8083 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 42 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F94 | 8085 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 43 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F96 | 8087 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 44 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F98 | 8089 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 45 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F9A | 8091 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 46 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F9C | 8093 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 47 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1F9E | 8095 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 48 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FA0 | 8097 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 49 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FA2 | 8099 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 50 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FA4 | 8101 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 51 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FA6 | 8103 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 52 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FA8 | 8105 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 53 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FAA | 8107 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 54 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FAC | 8109 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 55 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FAE | 8111 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 56 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FB0 | 8113 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 57 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FB2 | 8115 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 58 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FB4 | 8117 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 59 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FB6 | 8119 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 60 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FB8 | 8121 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 61 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FBA | 8123 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 62 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FBC | 8125 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 63 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FBE | 8127 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 64 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FC0 | 8129 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 65 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FC2 | 8131 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 66 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FC4 | 8133 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 67 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FC6 | 8135 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 68 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FC8 | 8137 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 69 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FCA | 8139 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 70 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FCC | 8141 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 71 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FCE | 8143 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 72 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FD0 | 8145 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 73 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FD2 | 8147 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 74 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FD4 | 8149 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 75 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FD6 | 8151 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 76 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FD8 | 8153 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 77 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FDA | 8155 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 78 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FDC | 8157 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 79 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FDE | 8159 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 80 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FE0 | 8161 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 81 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FE2 | 8163 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 82 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FE4 | 8165 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 83 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FE6 | 8167 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 84 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FE8 | 8169 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 85 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FEA | 8171 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 86 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FEC | 8173 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 87 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FEE | 8175 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 88 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FF0 | 8177 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 89 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FF2 | 8179 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 90 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FF4 | 8181 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 91 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FF6 | 8183 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 92 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FF8 | 8185 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 93 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FFA | 8187 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 94 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FFC | 8189 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 95 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x1FFE | 8191 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 96 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2000 | 8193 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 97 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2002 | 8195 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 98 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2004 | 8197 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 99 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2006 | 8199 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C of wireless device 100 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2008 | 8201 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 1 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x200A | 8203 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 2 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x200C | 8205 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 3 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x200E | 8207 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 4 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2010 | 8209 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 5 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2012 | 8211 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 6 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2014 | 8213 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 7 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2016 | 8215 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 8 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2018 | 8217 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 9 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x201A | 8219 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 10 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x201C | 8221 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 11 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x201E | 8223 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 12 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2020 | 8225 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 13 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2022 | 8227 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 14 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2024 | 8229 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 15 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2026 | 8231 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 16 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2028 | 8233 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 17 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x202A | 8235 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 18 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x202C | 8237 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 19 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x202E | 8239 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 20 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2030 | 8241 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 21 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2032 | 8243 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 22 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2034 | 8245 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 23 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2036 | 8247 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 24 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2038 | 8249 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 25 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x203A | 8251 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 26 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x203C | 8253 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 27 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x203E | 8255 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 28 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2040 | 8257 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 29 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2042 | 8259 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 30 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2044 | 8261 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 31 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2046 | 8263 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 32 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2048 | 8265 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 33 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x204A | 8267 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 34 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x204C | 8269 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 35 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x204E | 8271 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 36 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2050 | 8273 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 37 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2052 | 8275 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 38 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2054 | 8277 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 39 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2056 | 8279 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 40 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2058 | 8281 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 41 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x205A | 8283 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 42 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x205C | 8285 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 43 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x205E | 8287 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 44 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2060 | 8289 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 45 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2062 | 8291 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 46 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2064 | 8293 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 47 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2066 | 8295 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 48 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2068 | 8297 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 49 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x206A | 8299 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 50 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x206C | 8301 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 51 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x206E | 8303 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 52 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2070 | 8305 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 53 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2072 | 8307 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 54 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2074 | 8309 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 55 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2076 | 8311 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 56 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2078 | 8313 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 57 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x207A | 8315 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 58 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x207C | 8317 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 59 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x207E | 8319 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 60 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2080 | 8321 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 61 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2082 | 8323 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 62 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2084 | 8325 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 63 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2086 | 8327 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 64 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2088 | 8329 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 65 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x208A | 8331 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 66 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x208C | 8333 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 67 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x208E | 8335 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 68 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2090 | 8337 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 69 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2092 | 8339 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 70 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2094 | 8341 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 71 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2096 | 8343 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 72 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2098 | 8345 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 73 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x209A | 8347 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 74 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x209C | 8349 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 75 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x209E | 8351 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 76 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x20A0 | 8353 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 77 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x20A2 | 8355 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 78 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x20A4 | 8357 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 79 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x20A6 | 8359 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 80 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x20A8 | 8361 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 81 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x20AA | 8363 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 82 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x20AC | 8365 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 83 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x20AE | 8367 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 84 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x20B0 | 8369 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 85 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x20B2 | 8371 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 86 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x20B4 | 8373 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 87 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x20B6 | 8375 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 88 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x20B8 | 8377 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 89 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x20BA | 8379 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 90 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x20BC | 8381 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 91 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x20BE | 8383 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 92 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x20C0 | 8385 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 93 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x20C2 | 8387 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 94 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x20C4 | 8389 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 95 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x20C6 | 8391 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 96 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x20C8 | 8393 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 97 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x20CA | 8395 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 98 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x20CC | 8397 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 99 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x20CE | 8399 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A of wireless device 100 | x | x | x | [11 empty] | x
Voltage Metering Data | 0x2198 | 8601 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 1 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x219A | 8603 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 2 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x219C | 8605 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 3 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x219E | 8607 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 4 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21A0 | 8609 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 5 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21A2 | 8611 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 6 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21A4 | 8613 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 7 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21A6 | 8615 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 8 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21A8 | 8617 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 9 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21AA | 8619 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 10 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21AC | 8621 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 11 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21AE | 8623 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 12 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21B0 | 8625 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 13 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21B2 | 8627 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 14 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21B4 | 8629 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 15 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21B6 | 8631 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 16 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21B8 | 8633 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 17 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21BA | 8635 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 18 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21BC | 8637 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 19 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21BE | 8639 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 20 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21C0 | 8641 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 21 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21C2 | 8643 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 22 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21C4 | 8645 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 23 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21C6 | 8647 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 24 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21C8 | 8649 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 25 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21CA | 8651 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 26 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21CC | 8653 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 27 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21CE | 8655 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 28 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21D0 | 8657 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 29 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21D2 | 8659 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 30 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21D4 | 8661 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 31 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21D6 | 8663 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 32 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21D8 | 8665 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 33 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21DA | 8667 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 34 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21DC | 8669 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 35 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21DE | 8671 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 36 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21E0 | 8673 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 37 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21E2 | 8675 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 38 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21E4 | 8677 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 39 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21E6 | 8679 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 40 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21E8 | 8681 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 41 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21EA | 8683 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 42 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21EC | 8685 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 43 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21EE | 8687 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 44 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21F0 | 8689 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 45 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21F2 | 8691 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 46 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21F4 | 8693 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 47 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21F6 | 8695 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 48 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21F8 | 8697 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 49 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21FA | 8699 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 50 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21FC | 8701 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 51 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x21FE | 8703 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 52 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2200 | 8705 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 53 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2202 | 8707 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 54 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2204 | 8709 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 55 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2206 | 8711 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 56 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2208 | 8713 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 57 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x220A | 8715 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 58 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x220C | 8717 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 59 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x220E | 8719 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 60 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2210 | 8721 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 61 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2212 | 8723 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 62 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2214 | 8725 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 63 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2216 | 8727 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 64 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2218 | 8729 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 65 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x221A | 8731 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 66 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x221C | 8733 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 67 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x221E | 8735 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 68 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2220 | 8737 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 69 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2222 | 8739 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 70 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2224 | 8741 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 71 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2226 | 8743 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 72 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2228 | 8745 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 73 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x222A | 8747 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 74 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x222C | 8749 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 75 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x222E | 8751 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 76 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2230 | 8753 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 77 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2232 | 8755 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 78 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2234 | 8757 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 79 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2236 | 8759 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 80 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2238 | 8761 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 81 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x223A | 8763 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 82 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x223C | 8765 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 83 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x223E | 8767 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 84 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2240 | 8769 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 85 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2242 | 8771 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 86 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2244 | 8773 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 87 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2246 | 8775 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 88 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2248 | 8777 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 89 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x224A | 8779 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 90 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x224C | 8781 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 91 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x224E | 8783 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 92 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2250 | 8785 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 93 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2252 | 8787 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 94 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2254 | 8789 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 95 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2256 | 8791 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 96 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2258 | 8793 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 97 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x225A | 8795 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 98 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x225C | 8797 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 99 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x225E | 8799 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N of wireless device 100 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2260 | 8801 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 1 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2262 | 8803 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 2 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2264 | 8805 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 3 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2266 | 8807 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 4 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2268 | 8809 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 5 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x226A | 8811 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 6 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x226C | 8813 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 7 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x226E | 8815 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 8 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2270 | 8817 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 9 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2272 | 8819 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 10 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2274 | 8821 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 11 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2276 | 8823 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 12 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2278 | 8825 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 13 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x227A | 8827 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 14 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x227C | 8829 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 15 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x227E | 8831 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 16 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2280 | 8833 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 17 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2282 | 8835 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 18 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2284 | 8837 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 19 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2286 | 8839 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 20 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2288 | 8841 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 21 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x228A | 8843 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 22 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x228C | 8845 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 23 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x228E | 8847 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 24 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2290 | 8849 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 25 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2292 | 8851 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 26 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2294 | 8853 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 27 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2296 | 8855 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 28 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2298 | 8857 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 29 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x229A | 8859 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 30 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x229C | 8861 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 31 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x229E | 8863 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 32 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22A0 | 8865 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 33 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22A2 | 8867 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 34 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22A4 | 8869 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 35 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22A6 | 8871 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 36 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22A8 | 8873 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 37 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22AA | 8875 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 38 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22AC | 8877 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 39 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22AE | 8879 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 40 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22B0 | 8881 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 41 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22B2 | 8883 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 42 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22B4 | 8885 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 43 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22B6 | 8887 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 44 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22B8 | 8889 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 45 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22BA | 8891 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 46 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22BC | 8893 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 47 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22BE | 8895 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 48 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22C0 | 8897 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 49 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22C2 | 8899 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 50 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22C4 | 8901 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 51 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22C6 | 8903 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 52 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22C8 | 8905 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 53 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22CA | 8907 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 54 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22CC | 8909 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 55 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22CE | 8911 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 56 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22D0 | 8913 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 57 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22D2 | 8915 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 58 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22D4 | 8917 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 59 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22D6 | 8919 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 60 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22D8 | 8921 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 61 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22DA | 8923 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 62 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22DC | 8925 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 63 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22DE | 8927 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 64 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22E0 | 8929 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 65 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22E2 | 8931 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 66 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22E4 | 8933 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 67 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22E6 | 8935 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 68 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22E8 | 8937 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 69 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22EA | 8939 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 70 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22EC | 8941 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 71 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22EE | 8943 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 72 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22F0 | 8945 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 73 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22F2 | 8947 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 74 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22F4 | 8949 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 75 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22F6 | 8951 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 76 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22F8 | 8953 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 77 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22FA | 8955 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 78 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22FC | 8957 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 79 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x22FE | 8959 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 80 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2300 | 8961 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 81 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2302 | 8963 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 82 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2304 | 8965 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 83 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2306 | 8967 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 84 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2308 | 8969 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 85 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x230A | 8971 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 86 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x230C | 8973 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 87 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x230E | 8975 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 88 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2310 | 8977 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 89 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2312 | 8979 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 90 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2314 | 8981 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 91 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2316 | 8983 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 92 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2318 | 8985 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 93 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x231A | 8987 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 94 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x231C | 8989 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 95 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x231E | 8991 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 96 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2320 | 8993 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 97 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2322 | 8995 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 98 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2324 | 8997 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 99 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2326 | 8999 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N of wireless device 100 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2328 | 9001 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 1 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x232A | 9003 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 2 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x232C | 9005 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 3 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x232E | 9007 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 4 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2330 | 9009 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 5 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2332 | 9011 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 6 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2334 | 9013 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 7 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2336 | 9015 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 8 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2338 | 9017 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 9 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x233A | 9019 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 10 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x233C | 9021 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 11 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x233E | 9023 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 12 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2340 | 9025 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 13 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2342 | 9027 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 14 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2344 | 9029 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 15 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2346 | 9031 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 16 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2348 | 9033 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 17 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x234A | 9035 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 18 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x234C | 9037 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 19 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x234E | 9039 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 20 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2350 | 9041 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 21 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2352 | 9043 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 22 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2354 | 9045 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 23 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2356 | 9047 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 24 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2358 | 9049 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 25 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x235A | 9051 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 26 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x235C | 9053 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 27 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x235E | 9055 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 28 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2360 | 9057 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 29 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2362 | 9059 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 30 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2364 | 9061 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 31 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2366 | 9063 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 32 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2368 | 9065 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 33 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x236A | 9067 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 34 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x236C | 9069 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 35 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x236E | 9071 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 36 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2370 | 9073 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 37 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2372 | 9075 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 38 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2374 | 9077 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 39 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2376 | 9079 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 40 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2378 | 9081 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 41 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x237A | 9083 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 42 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x237C | 9085 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 43 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x237E | 9087 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 44 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2380 | 9089 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 45 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2382 | 9091 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 46 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2384 | 9093 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 47 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2386 | 9095 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 48 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2388 | 9097 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 49 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x238A | 9099 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 50 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x238C | 9101 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 51 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x238E | 9103 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 52 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2390 | 9105 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 53 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2392 | 9107 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 54 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2394 | 9109 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 55 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2396 | 9111 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 56 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x2398 | 9113 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 57 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x239A | 9115 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 58 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x239C | 9117 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 59 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x239E | 9119 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 60 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23A0 | 9121 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 61 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23A2 | 9123 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 62 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23A4 | 9125 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 63 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23A6 | 9127 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 64 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23A8 | 9129 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 65 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23AA | 9131 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 66 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23AC | 9133 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 67 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23AE | 9135 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 68 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23B0 | 9137 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 69 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23B2 | 9139 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 70 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23B4 | 9141 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 71 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23B6 | 9143 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 72 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23B8 | 9145 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 73 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23BA | 9147 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 74 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23BC | 9149 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 75 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23BE | 9151 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 76 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23C0 | 9153 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 77 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23C2 | 9155 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 78 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23C4 | 9157 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 79 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23C6 | 9159 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 80 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23C8 | 9161 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 81 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23CA | 9163 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 82 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23CC | 9165 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 83 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23CE | 9167 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 84 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23D0 | 9169 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 85 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23D2 | 9171 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 86 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23D4 | 9173 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 87 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23D6 | 9175 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 88 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23D8 | 9177 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 89 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23DA | 9179 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 90 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23DC | 9181 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 91 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23DE | 9183 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 92 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23E0 | 9185 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 93 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23E2 | 9187 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 94 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23E4 | 9189 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 95 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23E6 | 9191 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 96 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23E8 | 9193 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 97 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23EA | 9195 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 98 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23EC | 9197 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 99 | x | x | x | [5 empty] | x | [5 empty] | x
Voltage Metering Data | 0x23EE | 9199 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N of wireless device 100 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24B8 | 9401 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 1 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24BA | 9403 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 2 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24BC | 9405 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 3 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24BE | 9407 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 4 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24C0 | 9409 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 5 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24C2 | 9411 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 6 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24C4 | 9413 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 7 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24C6 | 9415 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 8 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24C8 | 9417 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 9 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24CA | 9419 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 10 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24CC | 9421 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 11 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24CE | 9423 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 12 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24D0 | 9425 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 13 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24D2 | 9427 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 14 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24D4 | 9429 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 15 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24D6 | 9431 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 16 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24D8 | 9433 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 17 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24DA | 9435 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 18 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24DC | 9437 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 19 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24DE | 9439 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 20 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24E0 | 9441 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 21 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24E2 | 9443 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 22 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24E4 | 9445 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 23 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24E6 | 9447 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 24 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24E8 | 9449 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 25 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24EA | 9451 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 26 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24EC | 9453 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 27 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24EE | 9455 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 28 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24F0 | 9457 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 29 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24F2 | 9459 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 30 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24F4 | 9461 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 31 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24F6 | 9463 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 32 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24F8 | 9465 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 33 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24FA | 9467 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 34 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24FC | 9469 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 35 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x24FE | 9471 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 36 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2500 | 9473 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 37 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2502 | 9475 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 38 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2504 | 9477 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 39 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2506 | 9479 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 40 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2508 | 9481 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 41 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x250A | 9483 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 42 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x250C | 9485 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 43 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x250E | 9487 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 44 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2510 | 9489 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 45 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2512 | 9491 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 46 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2514 | 9493 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 47 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2516 | 9495 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 48 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2518 | 9497 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 49 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x251A | 9499 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 50 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x251C | 9501 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 51 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x251E | 9503 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 52 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2520 | 9505 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 53 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2522 | 9507 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 54 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2524 | 9509 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 55 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2526 | 9511 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 56 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2528 | 9513 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 57 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x252A | 9515 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 58 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x252C | 9517 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 59 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x252E | 9519 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 60 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2530 | 9521 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 61 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2532 | 9523 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 62 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2534 | 9525 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 63 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2536 | 9527 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 64 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2538 | 9529 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 65 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x253A | 9531 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 66 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x253C | 9533 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 67 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x253E | 9535 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 68 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2540 | 9537 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 69 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2542 | 9539 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 70 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2544 | 9541 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 71 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2546 | 9543 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 72 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2548 | 9545 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 73 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x254A | 9547 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 74 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x254C | 9549 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 75 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x254E | 9551 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 76 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2550 | 9553 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 77 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2552 | 9555 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 78 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2554 | 9557 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 79 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2556 | 9559 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 80 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2558 | 9561 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 81 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x255A | 9563 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 82 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x255C | 9565 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 83 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x255E | 9567 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 84 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2560 | 9569 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 85 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2562 | 9571 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 86 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2564 | 9573 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 87 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2566 | 9575 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 88 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2568 | 9577 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 89 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x256A | 9579 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 90 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x256C | 9581 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 91 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x256E | 9583 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 92 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2570 | 9585 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 93 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2572 | 9587 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 94 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2574 | 9589 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 95 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2576 | 9591 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 96 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2578 | 9593 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 97 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x257A | 9595 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 98 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x257C | 9597 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 99 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x257E | 9599 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A of wireless device 100 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2580 | 9601 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 1 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2582 | 9603 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 2 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2584 | 9605 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 3 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2586 | 9607 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 4 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2588 | 9609 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 5 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x258A | 9611 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 6 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x258C | 9613 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 7 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x258E | 9615 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 8 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2590 | 9617 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 9 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2592 | 9619 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 10 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2594 | 9621 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 11 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2596 | 9623 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 12 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2598 | 9625 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 13 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x259A | 9627 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 14 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x259C | 9629 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 15 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x259E | 9631 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 16 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25A0 | 9633 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 17 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25A2 | 9635 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 18 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25A4 | 9637 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 19 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25A6 | 9639 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 20 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25A8 | 9641 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 21 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25AA | 9643 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 22 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25AC | 9645 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 23 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25AE | 9647 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 24 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25B0 | 9649 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 25 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25B2 | 9651 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 26 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25B4 | 9653 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 27 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25B6 | 9655 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 28 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25B8 | 9657 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 29 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25BA | 9659 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 30 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25BC | 9661 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 31 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25BE | 9663 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 32 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25C0 | 9665 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 33 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25C2 | 9667 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 34 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25C4 | 9669 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 35 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25C6 | 9671 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 36 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25C8 | 9673 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 37 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25CA | 9675 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 38 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25CC | 9677 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 39 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25CE | 9679 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 40 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25D0 | 9681 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 41 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25D2 | 9683 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 42 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25D4 | 9685 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 43 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25D6 | 9687 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 44 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25D8 | 9689 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 45 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25DA | 9691 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 46 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25DC | 9693 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 47 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25DE | 9695 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 48 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25E0 | 9697 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 49 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25E2 | 9699 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 50 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25E4 | 9701 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 51 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25E6 | 9703 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 52 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25E8 | 9705 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 53 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25EA | 9707 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 54 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25EC | 9709 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 55 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25EE | 9711 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 56 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25F0 | 9713 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 57 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25F2 | 9715 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 58 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25F4 | 9717 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 59 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25F6 | 9719 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 60 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25F8 | 9721 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 61 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25FA | 9723 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 62 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25FC | 9725 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 63 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x25FE | 9727 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 64 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2600 | 9729 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 65 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2602 | 9731 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 66 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2604 | 9733 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 67 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2606 | 9735 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 68 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2608 | 9737 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 69 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x260A | 9739 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 70 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x260C | 9741 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 71 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x260E | 9743 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 72 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2610 | 9745 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 73 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2612 | 9747 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 74 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2614 | 9749 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 75 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2616 | 9751 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 76 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2618 | 9753 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 77 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x261A | 9755 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 78 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x261C | 9757 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 79 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x261E | 9759 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 80 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2620 | 9761 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 81 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2622 | 9763 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 82 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2624 | 9765 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 83 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2626 | 9767 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 84 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2628 | 9769 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 85 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x262A | 9771 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 86 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x262C | 9773 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 87 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x262E | 9775 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 88 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2630 | 9777 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 89 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2632 | 9779 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 90 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2634 | 9781 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 91 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2636 | 9783 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 92 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2638 | 9785 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 93 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x263A | 9787 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 94 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x263C | 9789 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 95 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x263E | 9791 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 96 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2640 | 9793 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 97 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2642 | 9795 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 98 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2644 | 9797 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 99 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2646 | 9799 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B of wireless device 100 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2648 | 9801 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 1 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x264A | 9803 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 2 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x264C | 9805 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 3 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x264E | 9807 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 4 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2650 | 9809 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 5 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2652 | 9811 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 6 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2654 | 9813 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 7 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2656 | 9815 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 8 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2658 | 9817 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 9 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x265A | 9819 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 10 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x265C | 9821 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 11 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x265E | 9823 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 12 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2660 | 9825 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 13 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2662 | 9827 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 14 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2664 | 9829 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 15 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2666 | 9831 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 16 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2668 | 9833 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 17 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x266A | 9835 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 18 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x266C | 9837 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 19 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x266E | 9839 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 20 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2670 | 9841 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 21 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2672 | 9843 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 22 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2674 | 9845 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 23 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2676 | 9847 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 24 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2678 | 9849 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 25 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x267A | 9851 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 26 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x267C | 9853 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 27 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x267E | 9855 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 28 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2680 | 9857 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 29 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2682 | 9859 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 30 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2684 | 9861 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 31 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2686 | 9863 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 32 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2688 | 9865 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 33 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x268A | 9867 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 34 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x268C | 9869 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 35 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x268E | 9871 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 36 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2690 | 9873 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 37 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2692 | 9875 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 38 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2694 | 9877 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 39 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2696 | 9879 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 40 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2698 | 9881 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 41 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x269A | 9883 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 42 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x269C | 9885 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 43 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x269E | 9887 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 44 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26A0 | 9889 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 45 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26A2 | 9891 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 46 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26A4 | 9893 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 47 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26A6 | 9895 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 48 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26A8 | 9897 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 49 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26AA | 9899 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 50 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26AC | 9901 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 51 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26AE | 9903 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 52 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26B0 | 9905 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 53 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26B2 | 9907 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 54 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26B4 | 9909 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 55 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26B6 | 9911 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 56 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26B8 | 9913 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 57 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26BA | 9915 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 58 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26BC | 9917 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 59 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26BE | 9919 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 60 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26C0 | 9921 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 61 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26C2 | 9923 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 62 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26C4 | 9925 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 63 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26C6 | 9927 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 64 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26C8 | 9929 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 65 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26CA | 9931 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 66 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26CC | 9933 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 67 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26CE | 9935 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 68 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26D0 | 9937 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 69 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26D2 | 9939 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 70 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26D4 | 9941 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 71 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26D6 | 9943 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 72 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26D8 | 9945 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 73 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26DA | 9947 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 74 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26DC | 9949 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 75 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26DE | 9951 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 76 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26E0 | 9953 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 77 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26E2 | 9955 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 78 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26E4 | 9957 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 79 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26E6 | 9959 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 80 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26E8 | 9961 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 81 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26EA | 9963 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 82 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26EC | 9965 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 83 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26EE | 9967 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 84 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26F0 | 9969 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 85 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26F2 | 9971 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 86 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26F4 | 9973 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 87 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26F6 | 9975 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 88 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26F8 | 9977 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 89 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26FA | 9979 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 90 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26FC | 9981 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 91 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x26FE | 9983 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 92 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2700 | 9985 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 93 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2702 | 9987 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 94 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2704 | 9989 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 95 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2706 | 9991 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 96 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2708 | 9993 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 97 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x270A | 9995 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 98 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x270C | 9997 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 99 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x270E | 9999 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C of wireless device 100 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2710 | 10001 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 1 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2712 | 10003 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 2 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2714 | 10005 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 3 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2716 | 10007 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 4 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2718 | 10009 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 5 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x271A | 10011 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 6 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x271C | 10013 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 7 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x271E | 10015 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 8 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2720 | 10017 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 9 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2722 | 10019 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 10 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2724 | 10021 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 11 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2726 | 10023 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 12 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2728 | 10025 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 13 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x272A | 10027 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 14 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x272C | 10029 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 15 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x272E | 10031 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 16 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2730 | 10033 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 17 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2732 | 10035 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 18 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2734 | 10037 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 19 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2736 | 10039 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 20 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2738 | 10041 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 21 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x273A | 10043 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 22 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x273C | 10045 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 23 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x273E | 10047 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 24 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2740 | 10049 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 25 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2742 | 10051 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 26 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2744 | 10053 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 27 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2746 | 10055 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 28 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2748 | 10057 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 29 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x274A | 10059 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 30 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x274C | 10061 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 31 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x274E | 10063 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 32 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2750 | 10065 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 33 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2752 | 10067 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 34 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2754 | 10069 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 35 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2756 | 10071 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 36 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2758 | 10073 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 37 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x275A | 10075 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 38 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x275C | 10077 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 39 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x275E | 10079 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 40 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2760 | 10081 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 41 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2762 | 10083 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 42 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2764 | 10085 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 43 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2766 | 10087 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 44 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2768 | 10089 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 45 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x276A | 10091 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 46 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x276C | 10093 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 47 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x276E | 10095 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 48 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2770 | 10097 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 49 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2772 | 10099 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 50 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2774 | 10101 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 51 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2776 | 10103 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 52 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2778 | 10105 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 53 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x277A | 10107 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 54 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x277C | 10109 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 55 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x277E | 10111 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 56 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2780 | 10113 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 57 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2782 | 10115 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 58 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2784 | 10117 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 59 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2786 | 10119 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 60 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2788 | 10121 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 61 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x278A | 10123 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 62 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x278C | 10125 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 63 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x278E | 10127 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 64 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2790 | 10129 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 65 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2792 | 10131 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 66 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2794 | 10133 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 67 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2796 | 10135 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 68 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2798 | 10137 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 69 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x279A | 10139 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 70 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x279C | 10141 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 71 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x279E | 10143 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 72 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27A0 | 10145 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 73 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27A2 | 10147 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 74 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27A4 | 10149 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 75 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27A6 | 10151 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 76 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27A8 | 10153 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 77 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27AA | 10155 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 78 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27AC | 10157 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 79 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27AE | 10159 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 80 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27B0 | 10161 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 81 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27B2 | 10163 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 82 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27B4 | 10165 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 83 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27B6 | 10167 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 84 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27B8 | 10169 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 85 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27BA | 10171 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 86 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27BC | 10173 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 87 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27BE | 10175 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 88 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27C0 | 10177 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 89 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27C2 | 10179 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 90 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27C4 | 10181 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 91 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27C6 | 10183 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 92 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27C8 | 10185 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 93 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27CA | 10187 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 94 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27CC | 10189 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 95 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27CE | 10191 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 96 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27D0 | 10193 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 97 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27D2 | 10195 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 98 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27D4 | 10197 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 99 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27D6 | 10199 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power of wireless device 100 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27D8 | 10201 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 1 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27DA | 10203 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 2 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27DC | 10205 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 3 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27DE | 10207 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 4 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27E0 | 10209 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 5 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27E2 | 10211 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 6 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27E4 | 10213 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 7 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27E6 | 10215 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 8 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27E8 | 10217 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 9 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27EA | 10219 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 10 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27EC | 10221 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 11 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27EE | 10223 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 12 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27F0 | 10225 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 13 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27F2 | 10227 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 14 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27F4 | 10229 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 15 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27F6 | 10231 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 16 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27F8 | 10233 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 17 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27FA | 10235 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 18 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27FC | 10237 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 19 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x27FE | 10239 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 20 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2800 | 10241 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 21 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2802 | 10243 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 22 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2804 | 10245 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 23 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2806 | 10247 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 24 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2808 | 10249 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 25 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x280A | 10251 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 26 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x280C | 10253 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 27 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x280E | 10255 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 28 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2810 | 10257 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 29 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2812 | 10259 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 30 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2814 | 10261 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 31 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2816 | 10263 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 32 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2818 | 10265 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 33 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x281A | 10267 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 34 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x281C | 10269 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 35 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x281E | 10271 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 36 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2820 | 10273 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 37 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2822 | 10275 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 38 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2824 | 10277 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 39 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2826 | 10279 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 40 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2828 | 10281 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 41 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x282A | 10283 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 42 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x282C | 10285 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 43 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x282E | 10287 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 44 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2830 | 10289 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 45 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2832 | 10291 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 46 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2834 | 10293 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 47 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2836 | 10295 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 48 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2838 | 10297 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 49 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x283A | 10299 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 50 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x283C | 10301 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 51 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x283E | 10303 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 52 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2840 | 10305 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 53 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2842 | 10307 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 54 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2844 | 10309 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 55 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2846 | 10311 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 56 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2848 | 10313 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 57 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x284A | 10315 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 58 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x284C | 10317 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 59 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x284E | 10319 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 60 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2850 | 10321 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 61 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2852 | 10323 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 62 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2854 | 10325 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 63 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2856 | 10327 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 64 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2858 | 10329 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 65 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x285A | 10331 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 66 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x285C | 10333 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 67 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x285E | 10335 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 68 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2860 | 10337 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 69 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2862 | 10339 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 70 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2864 | 10341 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 71 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2866 | 10343 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 72 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2868 | 10345 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 73 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x286A | 10347 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 74 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x286C | 10349 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 75 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x286E | 10351 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 76 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2870 | 10353 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 77 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2872 | 10355 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 78 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2874 | 10357 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 79 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2876 | 10359 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 80 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2878 | 10361 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 81 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x287A | 10363 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 82 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x287C | 10365 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 83 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x287E | 10367 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 84 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2880 | 10369 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 85 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2882 | 10371 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 86 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2884 | 10373 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 87 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2886 | 10375 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 88 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2888 | 10377 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 89 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x288A | 10379 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 90 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x288C | 10381 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 91 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x288E | 10383 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 92 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2890 | 10385 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 93 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2892 | 10387 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 94 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2894 | 10389 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 95 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2896 | 10391 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 96 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2898 | 10393 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 97 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x289A | 10395 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 98 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x289C | 10397 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 99 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x289E | 10399 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power of wireless device 100 |  | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28A0 | 10401 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 1 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28A2 | 10403 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 2 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28A4 | 10405 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 3 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28A6 | 10407 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 4 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28A8 | 10409 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 5 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28AA | 10411 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 6 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28AC | 10413 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 7 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28AE | 10415 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 8 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28B0 | 10417 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 9 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28B2 | 10419 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 10 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28B4 | 10421 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 11 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28B6 | 10423 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 12 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28B8 | 10425 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 13 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28BA | 10427 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 14 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28BC | 10429 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 15 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28BE | 10431 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 16 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28C0 | 10433 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 17 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28C2 | 10435 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 18 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28C4 | 10437 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 19 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28C6 | 10439 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 20 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28C8 | 10441 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 21 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28CA | 10443 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 22 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28CC | 10445 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 23 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28CE | 10447 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 24 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28D0 | 10449 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 25 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28D2 | 10451 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 26 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28D4 | 10453 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 27 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28D6 | 10455 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 28 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28D8 | 10457 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 29 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28DA | 10459 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 30 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28DC | 10461 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 31 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28DE | 10463 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 32 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28E0 | 10465 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 33 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28E2 | 10467 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 34 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28E4 | 10469 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 35 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28E6 | 10471 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 36 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28E8 | 10473 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 37 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28EA | 10475 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 38 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28EC | 10477 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 39 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28EE | 10479 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 40 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28F0 | 10481 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 41 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28F2 | 10483 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 42 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28F4 | 10485 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 43 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28F6 | 10487 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 44 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28F8 | 10489 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 45 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28FA | 10491 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 46 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28FC | 10493 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 47 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x28FE | 10495 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 48 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2900 | 10497 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 49 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2902 | 10499 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 50 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2904 | 10501 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 51 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2906 | 10503 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 52 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2908 | 10505 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 53 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x290A | 10507 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 54 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x290C | 10509 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 55 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x290E | 10511 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 56 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2910 | 10513 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 57 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2912 | 10515 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 58 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2914 | 10517 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 59 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2916 | 10519 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 60 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2918 | 10521 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 61 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x291A | 10523 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 62 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x291C | 10525 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 63 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x291E | 10527 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 64 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2920 | 10529 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 65 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2922 | 10531 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 66 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2924 | 10533 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 67 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2926 | 10535 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 68 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2928 | 10537 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 69 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x292A | 10539 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 70 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x292C | 10541 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 71 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x292E | 10543 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 72 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2930 | 10545 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 73 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2932 | 10547 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 74 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2934 | 10549 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 75 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2936 | 10551 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 76 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2938 | 10553 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 77 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x293A | 10555 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 78 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x293C | 10557 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 79 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x293E | 10559 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 80 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2940 | 10561 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 81 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2942 | 10563 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 82 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2944 | 10565 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 83 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2946 | 10567 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 84 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2948 | 10569 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 85 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x294A | 10571 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 86 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x294C | 10573 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 87 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x294E | 10575 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 88 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2950 | 10577 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 89 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2952 | 10579 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 90 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2954 | 10581 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 91 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2956 | 10583 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 92 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2958 | 10585 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 93 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x295A | 10587 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 94 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x295C | 10589 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 95 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x295E | 10591 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 96 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2960 | 10593 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 97 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2962 | 10595 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 98 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2964 | 10597 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 99 | x | x | x | [5 empty] | x | [5 empty] | x
Power Metering Data | 0x2966 | 10599 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic) of wireless device 100 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2968 | 10601 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 1 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x296A | 10603 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 2 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x296C | 10605 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 3 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x296E | 10607 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 4 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2970 | 10609 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 5 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2972 | 10611 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 6 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2974 | 10613 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 7 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2976 | 10615 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 8 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2978 | 10617 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 9 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x297A | 10619 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 10 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x297C | 10621 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 11 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x297E | 10623 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 12 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2980 | 10625 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 13 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2982 | 10627 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 14 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2984 | 10629 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 15 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2986 | 10631 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 16 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2988 | 10633 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 17 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x298A | 10635 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 18 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x298C | 10637 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 19 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x298E | 10639 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 20 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2990 | 10641 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 21 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2992 | 10643 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 22 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2994 | 10645 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 23 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2996 | 10647 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 24 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2998 | 10649 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 25 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x299A | 10651 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 26 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x299C | 10653 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 27 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x299E | 10655 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 28 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29A0 | 10657 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 29 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29A2 | 10659 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 30 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29A4 | 10661 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 31 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29A6 | 10663 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 32 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29A8 | 10665 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 33 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29AA | 10667 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 34 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29AC | 10669 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 35 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29AE | 10671 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 36 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29B0 | 10673 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 37 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29B2 | 10675 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 38 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29B4 | 10677 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 39 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29B6 | 10679 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 40 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29B8 | 10681 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 41 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29BA | 10683 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 42 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29BC | 10685 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 43 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29BE | 10687 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 44 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29C0 | 10689 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 45 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29C2 | 10691 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 46 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29C4 | 10693 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 47 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29C6 | 10695 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 48 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29C8 | 10697 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 49 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29CA | 10699 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 50 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29CC | 10701 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 51 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29CE | 10703 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 52 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29D0 | 10705 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 53 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29D2 | 10707 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 54 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29D4 | 10709 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 55 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29D6 | 10711 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 56 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29D8 | 10713 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 57 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29DA | 10715 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 58 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29DC | 10717 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 59 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29DE | 10719 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 60 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29E0 | 10721 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 61 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29E2 | 10723 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 62 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29E4 | 10725 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 63 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29E6 | 10727 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 64 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29E8 | 10729 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 65 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29EA | 10731 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 66 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29EC | 10733 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 67 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29EE | 10735 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 68 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29F0 | 10737 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 69 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29F2 | 10739 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 70 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29F4 | 10741 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 71 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29F6 | 10743 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 72 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29F8 | 10745 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 73 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29FA | 10747 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 74 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29FC | 10749 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 75 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x29FE | 10751 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 76 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2A00 | 10753 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 77 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2A02 | 10755 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 78 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2A04 | 10757 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 79 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2A06 | 10759 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 80 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2A08 | 10761 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 81 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2A0A | 10763 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 82 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2A0C | 10765 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 83 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2A0E | 10767 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 84 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2A10 | 10769 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 85 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2A12 | 10771 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 86 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2A14 | 10773 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 87 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2A16 | 10775 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 88 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2A18 | 10777 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 89 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2A1A | 10779 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 90 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2A1C | 10781 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 91 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2A1E | 10783 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 92 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2A20 | 10785 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 93 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2A22 | 10787 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 94 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2A24 | 10789 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 95 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2A26 | 10791 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 96 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2A28 | 10793 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 97 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2A2A | 10795 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 98 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2A2C | 10797 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 99 | x | x | x | [5 empty] | x | [5 empty] | x
Power Factor Metering Data | 0x2A2E | 10799 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor of wireless device 100 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2A30 | 10801 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 1 | x | x | x | [5 empty] | x
Energy Data | 0x2A32 | 10803 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 2 | x | x | x | [5 empty] | x
Energy Data | 0x2A34 | 10805 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 3 | x | x | x | [5 empty] | x
Energy Data | 0x2A36 | 10807 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 4 | x | x | x | [5 empty] | x
Energy Data | 0x2A38 | 10809 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 5 | x | x | x | [5 empty] | x
Energy Data | 0x2A3A | 10811 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 6 | x | x | x | [5 empty] | x
Energy Data | 0x2A3C | 10813 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 7 | x | x | x | [5 empty] | x
Energy Data | 0x2A3E | 10815 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 8 | x | x | x | [5 empty] | x
Energy Data | 0x2A40 | 10817 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 9 | x | x | x | [5 empty] | x
Energy Data | 0x2A42 | 10819 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 10 | x | x | x | [5 empty] | x
Energy Data | 0x2A44 | 10821 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 11 | x | x | x | [5 empty] | x
Energy Data | 0x2A46 | 10823 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 12 | x | x | x | [5 empty] | x
Energy Data | 0x2A48 | 10825 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 13 | x | x | x | [5 empty] | x
Energy Data | 0x2A4A | 10827 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 14 | x | x | x | [5 empty] | x
Energy Data | 0x2A4C | 10829 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 15 | x | x | x | [5 empty] | x
Energy Data | 0x2A4E | 10831 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 16 | x | x | x | [5 empty] | x
Energy Data | 0x2A50 | 10833 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 17 | x | x | x | [5 empty] | x
Energy Data | 0x2A52 | 10835 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 18 | x | x | x | [5 empty] | x
Energy Data | 0x2A54 | 10837 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 19 | x | x | x | [5 empty] | x
Energy Data | 0x2A56 | 10839 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 20 | x | x | x | [5 empty] | x
Energy Data | 0x2A58 | 10841 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 21 | x | x | x | [5 empty] | x
Energy Data | 0x2A5A | 10843 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 22 | x | x | x | [5 empty] | x
Energy Data | 0x2A5C | 10845 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 23 | x | x | x | [5 empty] | x
Energy Data | 0x2A5E | 10847 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 24 | x | x | x | [5 empty] | x
Energy Data | 0x2A60 | 10849 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 25 | x | x | x | [5 empty] | x
Energy Data | 0x2A62 | 10851 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 26 | x | x | x | [5 empty] | x
Energy Data | 0x2A64 | 10853 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 27 | x | x | x | [5 empty] | x
Energy Data | 0x2A66 | 10855 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 28 | x | x | x | [5 empty] | x
Energy Data | 0x2A68 | 10857 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 29 | x | x | x | [5 empty] | x
Energy Data | 0x2A6A | 10859 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 30 | x | x | x | [5 empty] | x
Energy Data | 0x2A6C | 10861 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 31 | x | x | x | [5 empty] | x
Energy Data | 0x2A6E | 10863 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 32 | x | x | x | [5 empty] | x
Energy Data | 0x2A70 | 10865 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 33 | x | x | x | [5 empty] | x
Energy Data | 0x2A72 | 10867 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 34 | x | x | x | [5 empty] | x
Energy Data | 0x2A74 | 10869 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 35 | x | x | x | [5 empty] | x
Energy Data | 0x2A76 | 10871 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 36 | x | x | x | [5 empty] | x
Energy Data | 0x2A78 | 10873 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 37 | x | x | x | [5 empty] | x
Energy Data | 0x2A7A | 10875 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 38 | x | x | x | [5 empty] | x
Energy Data | 0x2A7C | 10877 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 39 | x | x | x | [5 empty] | x
Energy Data | 0x2A7E | 10879 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 40 | x | x | x | [5 empty] | x
Energy Data | 0x2A80 | 10881 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 41 | x | x | x | [5 empty] | x
Energy Data | 0x2A82 | 10883 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 42 | x | x | x | [5 empty] | x
Energy Data | 0x2A84 | 10885 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 43 | x | x | x | [5 empty] | x
Energy Data | 0x2A86 | 10887 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 44 | x | x | x | [5 empty] | x
Energy Data | 0x2A88 | 10889 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 45 | x | x | x | [5 empty] | x
Energy Data | 0x2A8A | 10891 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 46 | x | x | x | [5 empty] | x
Energy Data | 0x2A8C | 10893 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 47 | x | x | x | [5 empty] | x
Energy Data | 0x2A8E | 10895 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 48 | x | x | x | [5 empty] | x
Energy Data | 0x2A90 | 10897 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 49 | x | x | x | [5 empty] | x
Energy Data | 0x2A92 | 10899 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 50 | x | x | x | [5 empty] | x
Energy Data | 0x2A94 | 10901 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 51 | x | x | x | [5 empty] | x
Energy Data | 0x2A96 | 10903 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 52 | x | x | x | [5 empty] | x
Energy Data | 0x2A98 | 10905 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 53 | x | x | x | [5 empty] | x
Energy Data | 0x2A9A | 10907 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 54 | x | x | x | [5 empty] | x
Energy Data | 0x2A9C | 10909 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 55 | x | x | x | [5 empty] | x
Energy Data | 0x2A9E | 10911 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 56 | x | x | x | [5 empty] | x
Energy Data | 0x2AA0 | 10913 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 57 | x | x | x | [5 empty] | x
Energy Data | 0x2AA2 | 10915 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 58 | x | x | x | [5 empty] | x
Energy Data | 0x2AA4 | 10917 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 59 | x | x | x | [5 empty] | x
Energy Data | 0x2AA6 | 10919 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 60 | x | x | x | [5 empty] | x
Energy Data | 0x2AA8 | 10921 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 61 | x | x | x | [5 empty] | x
Energy Data | 0x2AAA | 10923 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 62 | x | x | x | [5 empty] | x
Energy Data | 0x2AAC | 10925 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 63 | x | x | x | [5 empty] | x
Energy Data | 0x2AAE | 10927 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 64 | x | x | x | [5 empty] | x
Energy Data | 0x2AB0 | 10929 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 65 | x | x | x | [5 empty] | x
Energy Data | 0x2AB2 | 10931 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 66 | x | x | x | [5 empty] | x
Energy Data | 0x2AB4 | 10933 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 67 | x | x | x | [5 empty] | x
Energy Data | 0x2AB6 | 10935 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 68 | x | x | x | [5 empty] | x
Energy Data | 0x2AB8 | 10937 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 69 | x | x | x | [5 empty] | x
Energy Data | 0x2ABA | 10939 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 70 | x | x | x | [5 empty] | x
Energy Data | 0x2ABC | 10941 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 71 | x | x | x | [5 empty] | x
Energy Data | 0x2ABE | 10943 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 72 | x | x | x | [5 empty] | x
Energy Data | 0x2AC0 | 10945 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 73 | x | x | x | [5 empty] | x
Energy Data | 0x2AC2 | 10947 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 74 | x | x | x | [5 empty] | x
Energy Data | 0x2AC4 | 10949 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 75 | x | x | x | [5 empty] | x
Energy Data | 0x2AC6 | 10951 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 76 | x | x | x | [5 empty] | x
Energy Data | 0x2AC8 | 10953 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 77 | x | x | x | [5 empty] | x
Energy Data | 0x2ACA | 10955 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 78 | x | x | x | [5 empty] | x
Energy Data | 0x2ACC | 10957 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 79 | x | x | x | [5 empty] | x
Energy Data | 0x2ACE | 10959 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 80 | x | x | x | [5 empty] | x
Energy Data | 0x2AD0 | 10961 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 81 | x | x | x | [5 empty] | x
Energy Data | 0x2AD2 | 10963 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 82 | x | x | x | [5 empty] | x
Energy Data | 0x2AD4 | 10965 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 83 | x | x | x | [5 empty] | x
Energy Data | 0x2AD6 | 10967 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 84 | x | x | x | [5 empty] | x
Energy Data | 0x2AD8 | 10969 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 85 | x | x | x | [5 empty] | x
Energy Data | 0x2ADA | 10971 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 86 | x | x | x | [5 empty] | x
Energy Data | 0x2ADC | 10973 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 87 | x | x | x | [5 empty] | x
Energy Data | 0x2ADE | 10975 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 88 | x | x | x | [5 empty] | x
Energy Data | 0x2AE0 | 10977 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 89 | x | x | x | [5 empty] | x
Energy Data | 0x2AE2 | 10979 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 90 | x | x | x | [5 empty] | x
Energy Data | 0x2AE4 | 10981 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 91 | x | x | x | [5 empty] | x
Energy Data | 0x2AE6 | 10983 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 92 | x | x | x | [5 empty] | x
Energy Data | 0x2AE8 | 10985 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 93 | x | x | x | [5 empty] | x
Energy Data | 0x2AEA | 10987 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 94 | x | x | x | [5 empty] | x
Energy Data | 0x2AEC | 10989 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 95 | x | x | x | [5 empty] | x
Energy Data | 0x2AEE | 10991 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 96 | x | x | x | [5 empty] | x
Energy Data | 0x2AF0 | 10993 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 97 | x | x | x | [5 empty] | x
Energy Data | 0x2AF2 | 10995 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 98 | x | x | x | [5 empty] | x
Energy Data | 0x2AF4 | 10997 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 99 | x | x | x | [5 empty] | x
Energy Data | 0x2AF6 | 10999 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered + received (not resettable) of wireless device 100 | x | x | x | [5 empty] | x
Energy Data | 0x2AF8 | 11001 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 1 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2AFA | 11003 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 2 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2AFC | 11005 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 3 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2AFE | 11007 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 4 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B00 | 11009 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 5 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B02 | 11011 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 6 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B04 | 11013 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 7 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B06 | 11015 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 8 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B08 | 11017 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 9 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B0A | 11019 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 10 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B0C | 11021 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 11 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B0E | 11023 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 12 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B10 | 11025 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 13 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B12 | 11027 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 14 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B14 | 11029 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 15 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B16 | 11031 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 16 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B18 | 11033 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 17 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B1A | 11035 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 18 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B1C | 11037 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 19 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B1E | 11039 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 20 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B20 | 11041 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 21 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B22 | 11043 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 22 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B24 | 11045 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 23 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B26 | 11047 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 24 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B28 | 11049 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 25 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B2A | 11051 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 26 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B2C | 11053 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 27 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B2E | 11055 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 28 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B30 | 11057 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 29 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B32 | 11059 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 30 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B34 | 11061 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 31 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B36 | 11063 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 32 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B38 | 11065 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 33 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B3A | 11067 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 34 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B3C | 11069 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 35 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B3E | 11071 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 36 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B40 | 11073 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 37 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B42 | 11075 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 38 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B44 | 11077 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 39 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B46 | 11079 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 40 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B48 | 11081 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 41 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B4A | 11083 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 42 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B4C | 11085 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 43 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B4E | 11087 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 44 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B50 | 11089 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 45 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B52 | 11091 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 46 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B54 | 11093 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 47 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B56 | 11095 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 48 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B58 | 11097 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 49 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B5A | 11099 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 50 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B5C | 11101 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 51 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B5E | 11103 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 52 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B60 | 11105 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 53 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B62 | 11107 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 54 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B64 | 11109 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 55 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B66 | 11111 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 56 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B68 | 11113 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 57 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B6A | 11115 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 58 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B6C | 11117 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 59 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B6E | 11119 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 60 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B70 | 11121 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 61 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B72 | 11123 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 62 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B74 | 11125 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 63 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B76 | 11127 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 64 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B78 | 11129 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 65 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B7A | 11131 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 66 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B7C | 11133 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 67 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B7E | 11135 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 68 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B80 | 11137 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 69 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B82 | 11139 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 70 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B84 | 11141 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 71 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B86 | 11143 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 72 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B88 | 11145 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 73 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B8A | 11147 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 74 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B8C | 11149 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 75 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B8E | 11151 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 76 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B90 | 11153 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 77 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B92 | 11155 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 78 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B94 | 11157 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 79 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B96 | 11159 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 80 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B98 | 11161 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 81 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B9A | 11163 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 82 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B9C | 11165 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 83 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2B9E | 11167 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 84 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2BA0 | 11169 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 85 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2BA2 | 11171 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 86 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2BA4 | 11173 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 87 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2BA6 | 11175 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 88 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2BA8 | 11177 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 89 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2BAA | 11179 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 90 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2BAC | 11181 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 91 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2BAE | 11183 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 92 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2BB0 | 11185 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 93 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2BB2 | 11187 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 94 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2BB4 | 11189 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 95 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2BB6 | 11191 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 96 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2BB8 | 11193 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 97 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2BBA | 11195 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 98 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2BBC | 11197 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 99 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2BBE | 11199 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Partial active energy delivered + received (resettable) of wireless device 100 | x | x | x | [5 empty] | x | [5 empty] | x
Energy Data | 0x2BC0 | 11201 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 1 | x | x | x
Energy Data | 0x2BC2 | 11203 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 2 | x | x | x
Energy Data | 0x2BC4 | 11205 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 3 | x | x | x
Energy Data | 0x2BC6 | 11207 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 4 | x | x | x
Energy Data | 0x2BC8 | 11209 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 5 | x | x | x
Energy Data | 0x2BCA | 11211 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 6 | x | x | x
Energy Data | 0x2BCC | 11213 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 7 | x | x | x
Energy Data | 0x2BCE | 11215 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 8 | x | x | x
Energy Data | 0x2BD0 | 11217 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 9 | x | x | x
Energy Data | 0x2BD2 | 11219 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 10 | x | x | x
Energy Data | 0x2BD4 | 11221 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 11 | x | x | x
Energy Data | 0x2BD6 | 11223 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 12 | x | x | x
Energy Data | 0x2BD8 | 11225 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 13 | x | x | x
Energy Data | 0x2BDA | 11227 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 14 | x | x | x
Energy Data | 0x2BDC | 11229 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 15 | x | x | x
Energy Data | 0x2BDE | 11231 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 16 | x | x | x
Energy Data | 0x2BE0 | 11233 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 17 | x | x | x
Energy Data | 0x2BE2 | 11235 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 18 | x | x | x
Energy Data | 0x2BE4 | 11237 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 19 | x | x | x
Energy Data | 0x2BE6 | 11239 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 20 | x | x | x
Energy Data | 0x2BE8 | 11241 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 21 | x | x | x
Energy Data | 0x2BEA | 11243 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 22 | x | x | x
Energy Data | 0x2BEC | 11245 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 23 | x | x | x
Energy Data | 0x2BEE | 11247 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 24 | x | x | x
Energy Data | 0x2BF0 | 11249 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 25 | x | x | x
Energy Data | 0x2BF2 | 11251 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 26 | x | x | x
Energy Data | 0x2BF4 | 11253 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 27 | x | x | x
Energy Data | 0x2BF6 | 11255 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 28 | x | x | x
Energy Data | 0x2BF8 | 11257 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 29 | x | x | x
Energy Data | 0x2BFA | 11259 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 30 | x | x | x
Energy Data | 0x2BFC | 11261 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 31 | x | x | x
Energy Data | 0x2BFE | 11263 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 32 | x | x | x
Energy Data | 0x2C00 | 11265 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 33 | x | x | x
Energy Data | 0x2C02 | 11267 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 34 | x | x | x
Energy Data | 0x2C04 | 11269 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 35 | x | x | x
Energy Data | 0x2C06 | 11271 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 36 | x | x | x
Energy Data | 0x2C08 | 11273 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 37 | x | x | x
Energy Data | 0x2C0A | 11275 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 38 | x | x | x
Energy Data | 0x2C0C | 11277 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 39 | x | x | x
Energy Data | 0x2C0E | 11279 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 40 | x | x | x
Energy Data | 0x2C10 | 11281 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 41 | x | x | x
Energy Data | 0x2C12 | 11283 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 42 | x | x | x
Energy Data | 0x2C14 | 11285 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 43 | x | x | x
Energy Data | 0x2C16 | 11287 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 44 | x | x | x
Energy Data | 0x2C18 | 11289 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 45 | x | x | x
Energy Data | 0x2C1A | 11291 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 46 | x | x | x
Energy Data | 0x2C1C | 11293 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 47 | x | x | x
Energy Data | 0x2C1E | 11295 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 48 | x | x | x
Energy Data | 0x2C20 | 11297 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 49 | x | x | x
Energy Data | 0x2C22 | 11299 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 50 | x | x | x
Energy Data | 0x2C24 | 11301 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 51 | x | x | x
Energy Data | 0x2C26 | 11303 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 52 | x | x | x
Energy Data | 0x2C28 | 11305 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 53 | x | x | x
Energy Data | 0x2C2A | 11307 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 54 | x | x | x
Energy Data | 0x2C2C | 11309 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 55 | x | x | x
Energy Data | 0x2C2E | 11311 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 56 | x | x | x
Energy Data | 0x2C30 | 11313 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 57 | x | x | x
Energy Data | 0x2C32 | 11315 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 58 | x | x | x
Energy Data | 0x2C34 | 11317 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 59 | x | x | x
Energy Data | 0x2C36 | 11319 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 60 | x | x | x
Energy Data | 0x2C38 | 11321 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 61 | x | x | x
Energy Data | 0x2C3A | 11323 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 62 | x | x | x
Energy Data | 0x2C3C | 11325 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 63 | x | x | x
Energy Data | 0x2C3E | 11327 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 64 | x | x | x
Energy Data | 0x2C40 | 11329 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 65 | x | x | x
Energy Data | 0x2C42 | 11331 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 66 | x | x | x
Energy Data | 0x2C44 | 11333 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 67 | x | x | x
Energy Data | 0x2C46 | 11335 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 68 | x | x | x
Energy Data | 0x2C48 | 11337 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 69 | x | x | x
Energy Data | 0x2C4A | 11339 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 70 | x | x | x
Energy Data | 0x2C4C | 11341 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 71 | x | x | x
Energy Data | 0x2C4E | 11343 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 72 | x | x | x
Energy Data | 0x2C50 | 11345 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 73 | x | x | x
Energy Data | 0x2C52 | 11347 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 74 | x | x | x
Energy Data | 0x2C54 | 11349 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 75 | x | x | x
Energy Data | 0x2C56 | 11351 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 76 | x | x | x
Energy Data | 0x2C58 | 11353 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 77 | x | x | x
Energy Data | 0x2C5A | 11355 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 78 | x | x | x
Energy Data | 0x2C5C | 11357 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 79 | x | x | x
Energy Data | 0x2C5E | 11359 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 80 | x | x | x
Energy Data | 0x2C60 | 11361 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 81 | x | x | x
Energy Data | 0x2C62 | 11363 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 82 | x | x | x
Energy Data | 0x2C64 | 11365 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 83 | x | x | x
Energy Data | 0x2C66 | 11367 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 84 | x | x | x
Energy Data | 0x2C68 | 11369 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 85 | x | x | x
Energy Data | 0x2C6A | 11371 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 86 | x | x | x
Energy Data | 0x2C6C | 11373 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 87 | x | x | x
Energy Data | 0x2C6E | 11375 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 88 | x | x | x
Energy Data | 0x2C70 | 11377 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 89 | x | x | x
Energy Data | 0x2C72 | 11379 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 90 | x | x | x
Energy Data | 0x2C74 | 11381 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 91 | x | x | x
Energy Data | 0x2C76 | 11383 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 92 | x | x | x
Energy Data | 0x2C78 | 11385 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 93 | x | x | x
Energy Data | 0x2C7A | 11387 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 94 | x | x | x
Energy Data | 0x2C7C | 11389 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 95 | x | x | x
Energy Data | 0x2C7E | 11391 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 96 | x | x | x
Energy Data | 0x2C80 | 11393 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 97 | x | x | x
Energy Data | 0x2C82 | 11395 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 98 | x | x | x
Energy Data | 0x2C84 | 11397 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 99 | x | x | x
Energy Data | 0x2C86 | 11399 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy delivered count positively (not resettable) of wireless device 100 | x | x | x
Energy Data | 0x2C88 | 11401 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 1 | x | x | x
Energy Data | 0x2C8A | 11403 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 2 | x | x | x
Energy Data | 0x2C8C | 11405 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 3 | x | x | x
Energy Data | 0x2C8E | 11407 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 4 | x | x | x
Energy Data | 0x2C90 | 11409 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 5 | x | x | x
Energy Data | 0x2C92 | 11411 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 6 | x | x | x
Energy Data | 0x2C94 | 11413 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 7 | x | x | x
Energy Data | 0x2C96 | 11415 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 8 | x | x | x
Energy Data | 0x2C98 | 11417 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 9 | x | x | x
Energy Data | 0x2C9A | 11419 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 10 | x | x | x
Energy Data | 0x2C9C | 11421 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 11 | x | x | x
Energy Data | 0x2C9E | 11423 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 12 | x | x | x
Energy Data | 0x2CA0 | 11425 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 13 | x | x | x
Energy Data | 0x2CA2 | 11427 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 14 | x | x | x
Energy Data | 0x2CA4 | 11429 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 15 | x | x | x
Energy Data | 0x2CA6 | 11431 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 16 | x | x | x
Energy Data | 0x2CA8 | 11433 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 17 | x | x | x
Energy Data | 0x2CAA | 11435 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 18 | x | x | x
Energy Data | 0x2CAC | 11437 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 19 | x | x | x
Energy Data | 0x2CAE | 11439 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 20 | x | x | x
Energy Data | 0x2CB0 | 11441 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 21 | x | x | x
Energy Data | 0x2CB2 | 11443 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 22 | x | x | x
Energy Data | 0x2CB4 | 11445 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 23 | x | x | x
Energy Data | 0x2CB6 | 11447 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 24 | x | x | x
Energy Data | 0x2CB8 | 11449 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 25 | x | x | x
Energy Data | 0x2CBA | 11451 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 26 | x | x | x
Energy Data | 0x2CBC | 11453 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 27 | x | x | x
Energy Data | 0x2CBE | 11455 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 28 | x | x | x
Energy Data | 0x2CC0 | 11457 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 29 | x | x | x
Energy Data | 0x2CC2 | 11459 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 30 | x | x | x
Energy Data | 0x2CC4 | 11461 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 31 | x | x | x
Energy Data | 0x2CC6 | 11463 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 32 | x | x | x
Energy Data | 0x2CC8 | 11465 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 33 | x | x | x
Energy Data | 0x2CCA | 11467 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 34 | x | x | x
Energy Data | 0x2CCC | 11469 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 35 | x | x | x
Energy Data | 0x2CCE | 11471 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 36 | x | x | x
Energy Data | 0x2CD0 | 11473 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 37 | x | x | x
Energy Data | 0x2CD2 | 11475 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 38 | x | x | x
Energy Data | 0x2CD4 | 11477 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 39 | x | x | x
Energy Data | 0x2CD6 | 11479 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 40 | x | x | x
Energy Data | 0x2CD8 | 11481 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 41 | x | x | x
Energy Data | 0x2CDA | 11483 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 42 | x | x | x
Energy Data | 0x2CDC | 11485 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 43 | x | x | x
Energy Data | 0x2CDE | 11487 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 44 | x | x | x
Energy Data | 0x2CE0 | 11489 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 45 | x | x | x
Energy Data | 0x2CE2 | 11491 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 46 | x | x | x
Energy Data | 0x2CE4 | 11493 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 47 | x | x | x
Energy Data | 0x2CE6 | 11495 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 48 | x | x | x
Energy Data | 0x2CE8 | 11497 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 49 | x | x | x
Energy Data | 0x2CEA | 11499 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 50 | x | x | x
Energy Data | 0x2CEC | 11501 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 51 | x | x | x
Energy Data | 0x2CEE | 11503 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 52 | x | x | x
Energy Data | 0x2CF0 | 11505 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 53 | x | x | x
Energy Data | 0x2CF2 | 11507 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 54 | x | x | x
Energy Data | 0x2CF4 | 11509 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 55 | x | x | x
Energy Data | 0x2CF6 | 11511 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 56 | x | x | x
Energy Data | 0x2CF8 | 11513 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 57 | x | x | x
Energy Data | 0x2CFA | 11515 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 58 | x | x | x
Energy Data | 0x2CFC | 11517 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 59 | x | x | x
Energy Data | 0x2CFE | 11519 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 60 | x | x | x
Energy Data | 0x2D00 | 11521 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 61 | x | x | x
Energy Data | 0x2D02 | 11523 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 62 | x | x | x
Energy Data | 0x2D04 | 11525 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 63 | x | x | x
Energy Data | 0x2D06 | 11527 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 64 | x | x | x
Energy Data | 0x2D08 | 11529 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 65 | x | x | x
Energy Data | 0x2D0A | 11531 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 66 | x | x | x
Energy Data | 0x2D0C | 11533 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 67 | x | x | x
Energy Data | 0x2D0E | 11535 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 68 | x | x | x
Energy Data | 0x2D10 | 11537 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 69 | x | x | x
Energy Data | 0x2D12 | 11539 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 70 | x | x | x
Energy Data | 0x2D14 | 11541 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 71 | x | x | x
Energy Data | 0x2D16 | 11543 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 72 | x | x | x
Energy Data | 0x2D18 | 11545 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 73 | x | x | x
Energy Data | 0x2D1A | 11547 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 74 | x | x | x
Energy Data | 0x2D1C | 11549 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 75 | x | x | x
Energy Data | 0x2D1E | 11551 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 76 | x | x | x
Energy Data | 0x2D20 | 11553 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 77 | x | x | x
Energy Data | 0x2D22 | 11555 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 78 | x | x | x
Energy Data | 0x2D24 | 11557 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 79 | x | x | x
Energy Data | 0x2D26 | 11559 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 80 | x | x | x
Energy Data | 0x2D28 | 11561 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 81 | x | x | x
Energy Data | 0x2D2A | 11563 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 82 | x | x | x
Energy Data | 0x2D2C | 11565 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 83 | x | x | x
Energy Data | 0x2D2E | 11567 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 84 | x | x | x
Energy Data | 0x2D30 | 11569 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 85 | x | x | x
Energy Data | 0x2D32 | 11571 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 86 | x | x | x
Energy Data | 0x2D34 | 11573 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 87 | x | x | x
Energy Data | 0x2D36 | 11575 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 88 | x | x | x
Energy Data | 0x2D38 | 11577 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 89 | x | x | x
Energy Data | 0x2D3A | 11579 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 90 | x | x | x
Energy Data | 0x2D3C | 11581 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 91 | x | x | x
Energy Data | 0x2D3E | 11583 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 92 | x | x | x
Energy Data | 0x2D40 | 11585 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 93 | x | x | x
Energy Data | 0x2D42 | 11587 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 94 | x | x | x
Energy Data | 0x2D44 | 11589 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 95 | x | x | x
Energy Data | 0x2D46 | 11591 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 96 | x | x | x
Energy Data | 0x2D48 | 11593 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 97 | x | x | x
Energy Data | 0x2D4A | 11595 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 98 | x | x | x
Energy Data | 0x2D4C | 11597 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 99 | x | x | x
Energy Data | 0x2D4E | 11599 | 2 | R | - | kWh | INT32 |  | 0x80000000 | N | 3, 100-4 | Total active energy received (not resettable) of wireless device 100 | x | x | x
Ambient Data | 0x7530 | 30001 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 1 |  |  |  | x | x | x | x | x
Ambient Data | 0x7532 | 30003 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 2 |  |  |  | x | x | x | x | x
Ambient Data | 0x7534 | 30005 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 3 |  |  |  | x | x | x | x | x
Ambient Data | 0x7536 | 30007 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 4 |  |  |  | x | x | x | x | x
Ambient Data | 0x7538 | 30009 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 5 |  |  |  | x | x | x | x | x
Ambient Data | 0x753A | 30011 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 6 |  |  |  | x | x | x | x | x
Ambient Data | 0x753C | 30013 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 7 |  |  |  | x | x | x | x | x
Ambient Data | 0x753E | 30015 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 8 |  |  |  | x | x | x | x | x
Ambient Data | 0x7540 | 30017 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 9 |  |  |  | x | x | x | x | x
Ambient Data | 0x7542 | 30019 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 10 |  |  |  | x | x | x | x | x
Ambient Data | 0x7544 | 30021 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 11 |  |  |  | x | x | x | x | x
Ambient Data | 0x7546 | 30023 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 12 |  |  |  | x | x | x | x | x
Ambient Data | 0x7548 | 30025 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 13 |  |  |  | x | x | x | x | x
Ambient Data | 0x754A | 30027 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 14 |  |  |  | x | x | x | x | x
Ambient Data | 0x754C | 30029 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 15 |  |  |  | x | x | x | x | x
Ambient Data | 0x754E | 30031 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 16 |  |  |  | x | x | x | x | x
Ambient Data | 0x7550 | 30033 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 17 |  |  |  | x | x | x | x | x
Ambient Data | 0x7552 | 30035 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 18 |  |  |  | x | x | x | x | x
Ambient Data | 0x7554 | 30037 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 19 |  |  |  | x | x | x | x | x
Ambient Data | 0x7556 | 30039 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 20 |  |  |  | x | x | x | x | x
Ambient Data | 0x7558 | 30041 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 21 |  |  |  | x | x | x | x | x
Ambient Data | 0x755A | 30043 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 22 |  |  |  | x | x | x | x | x
Ambient Data | 0x755C | 30045 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 23 |  |  |  | x | x | x | x | x
Ambient Data | 0x755E | 30047 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 24 |  |  |  | x | x | x | x | x
Ambient Data | 0x7560 | 30049 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 25 |  |  |  | x | x | x | x | x
Ambient Data | 0x7562 | 30051 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 26 |  |  |  | x | x | x | x | x
Ambient Data | 0x7564 | 30053 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 27 |  |  |  | x | x | x | x | x
Ambient Data | 0x7566 | 30055 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 28 |  |  |  | x | x | x | x | x
Ambient Data | 0x7568 | 30057 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 29 |  |  |  | x | x | x | x | x
Ambient Data | 0x756A | 30059 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 30 |  |  |  | x | x | x | x | x
Ambient Data | 0x756C | 30061 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 31 |  |  |  | x | x | x | x | x
Ambient Data | 0x756E | 30063 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 32 |  |  |  | x | x | x | x | x
Ambient Data | 0x7570 | 30065 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 33 |  |  |  | x | x | x | x | x
Ambient Data | 0x7572 | 30067 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 34 |  |  |  | x | x | x | x | x
Ambient Data | 0x7574 | 30069 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 35 |  |  |  | x | x | x | x | x
Ambient Data | 0x7576 | 30071 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 36 |  |  |  | x | x | x | x | x
Ambient Data | 0x7578 | 30073 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 37 |  |  |  | x | x | x | x | x
Ambient Data | 0x757A | 30075 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 38 |  |  |  | x | x | x | x | x
Ambient Data | 0x757C | 30077 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 39 |  |  |  | x | x | x | x | x
Ambient Data | 0x757E | 30079 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 40 |  |  |  | x | x | x | x | x
Ambient Data | 0x7580 | 30081 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 41 |  |  |  | x | x | x | x | x
Ambient Data | 0x7582 | 30083 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 42 |  |  |  | x | x | x | x | x
Ambient Data | 0x7584 | 30085 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 43 |  |  |  | x | x | x | x | x
Ambient Data | 0x7586 | 30087 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 44 |  |  |  | x | x | x | x | x
Ambient Data | 0x7588 | 30089 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 45 |  |  |  | x | x | x | x | x
Ambient Data | 0x758A | 30091 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 46 |  |  |  | x | x | x | x | x
Ambient Data | 0x758C | 30093 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 47 |  |  |  | x | x | x | x | x
Ambient Data | 0x758E | 30095 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 48 |  |  |  | x | x | x | x | x
Ambient Data | 0x7590 | 30097 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 49 |  |  |  | x | x | x | x | x
Ambient Data | 0x7592 | 30099 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 50 |  |  |  | x | x | x | x | x
Ambient Data | 0x7594 | 30101 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 51 |  |  |  | x | x | x | x | x
Ambient Data | 0x7596 | 30103 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 52 |  |  |  | x | x | x | x | x
Ambient Data | 0x7598 | 30105 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 53 |  |  |  | x | x | x | x | x
Ambient Data | 0x759A | 30107 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 54 |  |  |  | x | x | x | x | x
Ambient Data | 0x759C | 30109 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 55 |  |  |  | x | x | x | x | x
Ambient Data | 0x759E | 30111 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 56 |  |  |  | x | x | x | x | x
Ambient Data | 0x75A0 | 30113 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 57 |  |  |  | x | x | x | x | x
Ambient Data | 0x75A2 | 30115 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 58 |  |  |  | x | x | x | x | x
Ambient Data | 0x75A4 | 30117 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 59 |  |  |  | x | x | x | x | x
Ambient Data | 0x75A6 | 30119 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 60 |  |  |  | x | x | x | x | x
Ambient Data | 0x75A8 | 30121 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 61 |  |  |  | x | x | x | x | x
Ambient Data | 0x75AA | 30123 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 62 |  |  |  | x | x | x | x | x
Ambient Data | 0x75AC | 30125 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 63 |  |  |  | x | x | x | x | x
Ambient Data | 0x75AE | 30127 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 64 |  |  |  | x | x | x | x | x
Ambient Data | 0x75B0 | 30129 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 65 |  |  |  | x | x | x | x | x
Ambient Data | 0x75B2 | 30131 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 66 |  |  |  | x | x | x | x | x
Ambient Data | 0x75B4 | 30133 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 67 |  |  |  | x | x | x | x | x
Ambient Data | 0x75B6 | 30135 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 68 |  |  |  | x | x | x | x | x
Ambient Data | 0x75B8 | 30137 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 69 |  |  |  | x | x | x | x | x
Ambient Data | 0x75BA | 30139 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 70 |  |  |  | x | x | x | x | x
Ambient Data | 0x75BC | 30141 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 71 |  |  |  | x | x | x | x | x
Ambient Data | 0x75BE | 30143 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 72 |  |  |  | x | x | x | x | x
Ambient Data | 0x75C0 | 30145 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 73 |  |  |  | x | x | x | x | x
Ambient Data | 0x75C2 | 30147 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 74 |  |  |  | x | x | x | x | x
Ambient Data | 0x75C4 | 30149 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 75 |  |  |  | x | x | x | x | x
Ambient Data | 0x75C6 | 30151 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 76 |  |  |  | x | x | x | x | x
Ambient Data | 0x75C8 | 30153 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 77 |  |  |  | x | x | x | x | x
Ambient Data | 0x75CA | 30155 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 78 |  |  |  | x | x | x | x | x
Ambient Data | 0x75CC | 30157 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 79 |  |  |  | x | x | x | x | x
Ambient Data | 0x75CE | 30159 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 80 |  |  |  | x | x | x | x | x
Ambient Data | 0x75D0 | 30161 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 81 |  |  |  | x | x | x | x | x
Ambient Data | 0x75D2 | 30163 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 82 |  |  |  | x | x | x | x | x
Ambient Data | 0x75D4 | 30165 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 83 |  |  |  | x | x | x | x | x
Ambient Data | 0x75D6 | 30167 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 84 |  |  |  | x | x | x | x | x
Ambient Data | 0x75D8 | 30169 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 85 |  |  |  | x | x | x | x | x
Ambient Data | 0x75DA | 30171 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 86 |  |  |  | x | x | x | x | x
Ambient Data | 0x75DC | 30173 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 87 |  |  |  | x | x | x | x | x
Ambient Data | 0x75DE | 30175 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 88 |  |  |  | x | x | x | x | x
Ambient Data | 0x75E0 | 30177 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 89 |  |  |  | x | x | x | x | x
Ambient Data | 0x75E2 | 30179 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 90 |  |  |  | x | x | x | x | x
Ambient Data | 0x75E4 | 30181 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 91 |  |  |  | x | x | x | x | x
Ambient Data | 0x75E6 | 30183 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 92 |  |  |  | x | x | x | x | x
Ambient Data | 0x75E8 | 30185 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 93 |  |  |  | x | x | x | x | x
Ambient Data | 0x75EA | 30187 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 94 |  |  |  | x | x | x | x | x
Ambient Data | 0x75EC | 30189 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 95 |  |  |  | x | x | x | x | x
Ambient Data | 0x75EE | 30191 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 96 |  |  |  | x | x | x | x | x
Ambient Data | 0x75F0 | 30193 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 97 |  |  |  | x | x | x | x | x
Ambient Data | 0x75F2 | 30195 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 98 |  |  |  | x | x | x | x | x
Ambient Data | 0x75F4 | 30197 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 99 |  |  |  | x | x | x | x | x
Ambient Data | 0x75F6 | 30199 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value of wireless device 100 |  |  |  | x | x | x | x | x
Ambient Data | 0x75F8 | 30201 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 1 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x75FA | 30203 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 2 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x75FC | 30205 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 3 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x75FE | 30207 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 4 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7600 | 30209 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 5 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7602 | 30211 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 6 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7604 | 30213 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 7 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7606 | 30215 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 8 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7608 | 30217 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 9 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x760A | 30219 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 10 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x760C | 30221 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 11 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x760E | 30223 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 12 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7610 | 30225 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 13 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7612 | 30227 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 14 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7614 | 30229 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 15 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7616 | 30231 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 16 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7618 | 30233 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 17 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x761A | 30235 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 18 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x761C | 30237 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 19 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x761E | 30239 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 20 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7620 | 30241 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 21 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7622 | 30243 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 22 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7624 | 30245 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 23 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7626 | 30247 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 24 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7628 | 30249 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 25 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x762A | 30251 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 26 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x762C | 30253 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 27 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x762E | 30255 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 28 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7630 | 30257 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 29 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7632 | 30259 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 30 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7634 | 30261 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 31 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7636 | 30263 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 32 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7638 | 30265 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 33 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x763A | 30267 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 34 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x763C | 30269 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 35 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x763E | 30271 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 36 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7640 | 30273 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 37 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7642 | 30275 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 38 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7644 | 30277 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 39 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7646 | 30279 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 40 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7648 | 30281 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 41 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x764A | 30283 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 42 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x764C | 30285 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 43 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x764E | 30287 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 44 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7650 | 30289 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 45 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7652 | 30291 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 46 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7654 | 30293 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 47 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7656 | 30295 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 48 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7658 | 30297 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 49 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x765A | 30299 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 50 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x765C | 30301 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 51 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x765E | 30303 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 52 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7660 | 30305 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 53 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7662 | 30307 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 54 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7664 | 30309 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 55 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7666 | 30311 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 56 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7668 | 30313 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 57 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x766A | 30315 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 58 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x766C | 30317 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 59 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x766E | 30319 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 60 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7670 | 30321 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 61 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7672 | 30323 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 62 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7674 | 30325 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 63 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7676 | 30327 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 64 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7678 | 30329 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 65 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x767A | 30331 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 66 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x767C | 30333 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 67 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x767E | 30335 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 68 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7680 | 30337 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 69 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7682 | 30339 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 70 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7684 | 30341 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 71 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7686 | 30343 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 72 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7688 | 30345 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 73 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x768A | 30347 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 74 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x768C | 30349 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 75 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x768E | 30351 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 76 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7690 | 30353 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 77 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7692 | 30355 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 78 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7694 | 30357 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 79 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7696 | 30359 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 80 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x7698 | 30361 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 81 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x769A | 30363 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 82 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x769C | 30365 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 83 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x769E | 30367 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 84 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x76A0 | 30369 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 85 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x76A2 | 30371 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 86 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x76A4 | 30373 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 87 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x76A6 | 30375 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 88 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x76A8 | 30377 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 89 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x76AA | 30379 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 90 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x76AC | 30381 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 91 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x76AE | 30383 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 92 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x76B0 | 30385 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 93 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x76B2 | 30387 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 94 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x76B4 | 30389 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 95 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x76B6 | 30391 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 96 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x76B8 | 30393 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 97 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x76BA | 30395 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 98 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x76BC | 30397 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 99 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x76BE | 30399 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value of wireless device 100 Example: 50% represented as 0.50 |  |  |  |  | x | x | x | x
Ambient Data | 0x76C0 | 30401 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 1 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x76C2 | 30403 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 2 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x76C4 | 30405 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 3 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x76C6 | 30407 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 4 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x76C8 | 30409 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 5 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x76CA | 30411 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 6 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x76CC | 30413 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 7 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x76CE | 30415 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 8 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x76D0 | 30417 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 9 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x76D2 | 30419 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 10 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x76D4 | 30421 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 11 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x76D6 | 30423 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 12 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x76D8 | 30425 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 13 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x76DA | 30427 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 14 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x76DC | 30429 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 15 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x76DE | 30431 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 16 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x76E0 | 30433 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 17 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x76E2 | 30435 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 18 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x76E4 | 30437 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 19 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x76E6 | 30439 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 20 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x76E8 | 30441 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 21 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x76EA | 30443 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 22 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x76EC | 30445 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 23 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x76EE | 30447 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 24 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x76F0 | 30449 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 25 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x76F2 | 30451 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 26 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x76F4 | 30453 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 27 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x76F6 | 30455 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 28 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x76F8 | 30457 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 29 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x76FA | 30459 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 30 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x76FC | 30461 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 31 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x76FE | 30463 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 32 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7700 | 30465 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 33 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7702 | 30467 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 34 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7704 | 30469 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 35 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7706 | 30471 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 36 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7708 | 30473 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 37 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x770A | 30475 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 38 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x770C | 30477 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 39 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x770E | 30479 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 40 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7710 | 30481 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 41 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7712 | 30483 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 42 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7714 | 30485 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 43 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7716 | 30487 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 44 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7718 | 30489 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 45 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x771A | 30491 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 46 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x771C | 30493 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 47 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x771E | 30495 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 48 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7720 | 30497 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 49 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7722 | 30499 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 50 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7724 | 30501 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 51 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7726 | 30503 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 52 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7728 | 30505 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 53 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x772A | 30507 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 54 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x772C | 30509 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 55 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x772E | 30511 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 56 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7730 | 30513 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 57 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7732 | 30515 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 58 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7734 | 30517 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 59 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7736 | 30519 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 60 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7738 | 30521 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 61 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x773A | 30523 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 62 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x773C | 30525 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 63 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x773E | 30527 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 64 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7740 | 30529 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 65 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7742 | 30531 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 66 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7744 | 30533 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 67 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7746 | 30535 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 68 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7748 | 30537 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 69 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x774A | 30539 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 70 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x774C | 30541 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 71 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x774E | 30543 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 72 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7750 | 30545 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 73 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7752 | 30547 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 74 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7754 | 30549 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 75 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7756 | 30551 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 76 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7758 | 30553 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 77 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x775A | 30555 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 78 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x775C | 30557 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 79 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x775E | 30559 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 80 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7760 | 30561 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 81 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7762 | 30563 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 82 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7764 | 30565 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 83 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7766 | 30567 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 84 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7768 | 30569 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 85 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x776A | 30571 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 86 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x776C | 30573 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 87 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x776E | 30575 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 88 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7770 | 30577 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 89 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7772 | 30579 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 90 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7774 | 30581 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 91 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7776 | 30583 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 92 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7778 | 30585 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 93 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x777A | 30587 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 94 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x777C | 30589 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 95 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x777E | 30591 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 96 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7780 | 30593 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 97 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7782 | 30595 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 98 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7784 | 30597 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 99 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Ambient Data | 0x7786 | 30599 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index of wireless device 100 • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323) | [7 empty] | x
Device Temperature Metering Data | 0x7788 | 30601 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 1 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x778A | 30603 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 2 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x778C | 30605 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 3 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x778E | 30607 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 4 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x7790 | 30609 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 5 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x7792 | 30611 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 6 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x7794 | 30613 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 7 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x7796 | 30615 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 8 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x7798 | 30617 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 9 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x779A | 30619 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 10 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x779C | 30621 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 11 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x779E | 30623 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 12 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77A0 | 30625 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 13 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77A2 | 30627 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 14 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77A4 | 30629 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 15 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77A6 | 30631 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 16 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77A8 | 30633 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 17 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77AA | 30635 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 18 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77AC | 30637 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 19 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77AE | 30639 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 20 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77B0 | 30641 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 21 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77B2 | 30643 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 22 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77B4 | 30645 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 23 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77B6 | 30647 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 24 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77B8 | 30649 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 25 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77BA | 30651 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 26 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77BC | 30653 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 27 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77BE | 30655 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 28 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77C0 | 30657 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 29 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77C2 | 30659 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 30 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77C4 | 30661 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 31 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77C6 | 30663 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 32 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77C8 | 30665 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 33 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77CA | 30667 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 34 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77CC | 30669 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 35 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77CE | 30671 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 36 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77D0 | 30673 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 37 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77D2 | 30675 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 38 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77D4 | 30677 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 39 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77D6 | 30679 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 40 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77D8 | 30681 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 41 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77DA | 30683 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 42 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77DC | 30685 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 43 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77DE | 30687 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 44 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77E0 | 30689 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 45 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77E2 | 30691 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 46 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77E4 | 30693 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 47 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77E6 | 30695 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 48 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77E8 | 30697 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 49 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77EA | 30699 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 50 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77EC | 30701 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 51 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77EE | 30703 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 52 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77F0 | 30705 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 53 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77F2 | 30707 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 54 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77F4 | 30709 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 55 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77F6 | 30711 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 56 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77F8 | 30713 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 57 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77FA | 30715 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 58 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77FC | 30717 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 59 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x77FE | 30719 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 60 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x7800 | 30721 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 61 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x7802 | 30723 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 62 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x7804 | 30725 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 63 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x7806 | 30727 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 64 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x7808 | 30729 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 65 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x780A | 30731 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 66 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x780C | 30733 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 67 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x780E | 30735 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 68 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x7810 | 30737 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 69 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x7812 | 30739 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 70 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x7814 | 30741 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 71 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x7816 | 30743 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 72 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x7818 | 30745 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 73 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x781A | 30747 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 74 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x781C | 30749 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 75 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x781E | 30751 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 76 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x7820 | 30753 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 77 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x7822 | 30755 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 78 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x7824 | 30757 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 79 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x7826 | 30759 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 80 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x7828 | 30761 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 81 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x782A | 30763 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 82 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x782C | 30765 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 83 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x782E | 30767 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 84 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x7830 | 30769 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 85 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x7832 | 30771 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 86 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x7834 | 30773 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 87 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x7836 | 30775 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 88 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x7838 | 30777 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 89 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x783A | 30779 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 90 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x783C | 30781 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 91 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x783E | 30783 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 92 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x7840 | 30785 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 93 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x7842 | 30787 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 94 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x7844 | 30789 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 95 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x7846 | 30791 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 96 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x7848 | 30793 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 97 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x784A | 30795 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 98 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x784C | 30797 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 99 | x | x | x | x |  |  |  | x | x | x
Device Temperature Metering Data | 0x784E | 30799 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature of wireless device 100 | x | x | x | x |  |  |  | x | x | x
Load Monitoring - Alarm | 0x88BA | 35003 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 1 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88BB | 35004 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 1 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active
Load Monitoring - Alarm | 0x88BC | 35005 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 1 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88BD | 35006 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 1 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active
Load Monitoring - Alarm | 0x88BE | 35007 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 2 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88BF | 35008 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 2 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88C0 | 35009 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 2 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88C1 | 35010 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 2 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88C2 | 35011 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 3 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88C3 | 35012 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 3 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88C4 | 35013 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 3 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88C5 | 35014 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 3 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88C6 | 35015 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 4 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88C7 | 35016 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 4 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88C8 | 35017 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 4 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88C9 | 35018 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 4 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88CA | 35019 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 5 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88CB | 35020 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 5 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88CC | 35021 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 5 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88CD | 35022 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 5 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88CE | 35023 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 6 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88CF | 35024 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 6 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88D0 | 35025 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 6 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88D1 | 35026 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 6 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88D2 | 35027 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 7 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88D3 | 35028 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 7 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88D4 | 35029 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 7 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88D5 | 35030 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 7 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88D6 | 35031 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 8 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88D7 | 35032 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 8 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88D8 | 35033 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 8 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88D9 | 35034 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 8 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88DA | 35035 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 9 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88DB | 35036 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 9 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88DC | 35037 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 9 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88DD | 35038 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 9 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88DE | 35039 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 10 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88DF | 35040 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 10 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88E0 | 35041 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 10 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88E1 | 35042 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 10 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88E2 | 35043 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 11 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88E3 | 35044 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 11 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88E4 | 35045 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 11 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88E5 | 35046 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 11 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88E6 | 35047 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 12 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88E7 | 35048 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 12 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88E8 | 35049 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 12 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88E9 | 35050 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 12 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88EA | 35051 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 13 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88EB | 35052 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 13 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88EC | 35053 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 13 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88ED | 35054 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 13 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88EE | 35055 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 14 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88EF | 35056 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 14 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88F0 | 35057 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 14 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88F1 | 35058 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 14 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88F2 | 35059 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 15 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88F3 | 35060 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 15 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88F4 | 35061 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 15 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88F5 | 35062 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 15 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88F6 | 35063 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 16 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88F7 | 35064 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 16 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88F8 | 35065 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 16 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88F9 | 35066 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 16 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88FA | 35067 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 17 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88FB | 35068 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 17 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88FC | 35069 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 17 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88FD | 35070 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 17 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88FE | 35071 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 18 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x88FF | 35072 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 18 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8900 | 35073 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 18 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8901 | 35074 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 18 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8902 | 35075 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 19 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8903 | 35076 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 19 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8904 | 35077 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 19 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8905 | 35078 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 19 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8906 | 35079 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 20 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8907 | 35080 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 20 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8908 | 35081 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 20 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8909 | 35082 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 20 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x890A | 35083 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 21 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x890B | 35084 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 21 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x890C | 35085 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 21 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x890D | 35086 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 21 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x890E | 35087 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 22 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x890F | 35088 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 22 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8910 | 35089 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 22 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8911 | 35090 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 22 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8912 | 35091 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 23 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8913 | 35092 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 23 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8914 | 35093 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 23 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8915 | 35094 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 23 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8916 | 35095 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 24 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8917 | 35096 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 24 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8918 | 35097 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 24 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8919 | 35098 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 24 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x891A | 35099 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 25 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x891B | 35100 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 25 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x891C | 35101 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 25 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x891D | 35102 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 25 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x891E | 35103 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 26 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x891F | 35104 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 26 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8920 | 35105 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 26 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8921 | 35106 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 26 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8922 | 35107 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 27 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8923 | 35108 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 27 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8924 | 35109 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 27 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8925 | 35110 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 27 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8926 | 35111 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 28 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8927 | 35112 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 28 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8928 | 35113 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 28 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8929 | 35114 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 28 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x892A | 35115 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 29 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x892B | 35116 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 29 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x892C | 35117 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 29 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x892D | 35118 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 29 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x892E | 35119 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 30 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x892F | 35120 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 30 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8930 | 35121 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 30 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8931 | 35122 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 30 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8932 | 35123 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 31 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8933 | 35124 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 31 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8934 | 35125 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 31 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8935 | 35126 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 31 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8936 | 35127 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 32 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8937 | 35128 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 32 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8938 | 35129 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 32 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8939 | 35130 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 32 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x893A | 35131 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 33 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x893B | 35132 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 33 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x893C | 35133 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 33 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x893D | 35134 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 33 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x893E | 35135 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 34 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x893F | 35136 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 34 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8940 | 35137 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 34 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8941 | 35138 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 34 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8942 | 35139 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 35 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8943 | 35140 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 35 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8944 | 35141 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 35 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8945 | 35142 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 35 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8946 | 35143 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 36 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8947 | 35144 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 36 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8948 | 35145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 36 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8949 | 35146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 36 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x894A | 35147 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 37 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x894B | 35148 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 37 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x894C | 35149 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 37 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x894D | 35150 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 37 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x894E | 35151 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 38 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x894F | 35152 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 38 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8950 | 35153 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 38 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8951 | 35154 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 38 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8952 | 35155 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 39 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8953 | 35156 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 39 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8954 | 35157 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 39 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8955 | 35158 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 39 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8956 | 35159 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 40 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8957 | 35160 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 40 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8958 | 35161 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 40 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8959 | 35162 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 40 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x895A | 35163 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 41 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x895B | 35164 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 41 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x895C | 35165 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 41 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x895D | 35166 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 41 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x895E | 35167 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 42 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x895F | 35168 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 42 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8960 | 35169 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 42 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8961 | 35170 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 42 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8962 | 35171 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 43 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8963 | 35172 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 43 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8964 | 35173 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 43 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8965 | 35174 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 43 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8966 | 35175 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 44 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8967 | 35176 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 44 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8968 | 35177 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 44 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8969 | 35178 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 44 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x896A | 35179 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 45 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x896B | 35180 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 45 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x896C | 35181 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 45 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x896D | 35182 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 45 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x896E | 35183 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 46 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x896F | 35184 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 46 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8970 | 35185 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 46 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8971 | 35186 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 46 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8972 | 35187 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 47 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8973 | 35188 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 47 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8974 | 35189 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 47 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8975 | 35190 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 47 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8976 | 35191 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 48 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8977 | 35192 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 48 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8978 | 35193 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 48 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8979 | 35194 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 48 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x897A | 35195 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 49 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x897B | 35196 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 49 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x897C | 35197 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 49 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x897D | 35198 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 49 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x897E | 35199 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 50 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x897F | 35200 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 50 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8980 | 35201 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 50 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8981 | 35202 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 50 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8982 | 35203 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 51 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8983 | 35204 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 51 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8984 | 35205 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 51 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8985 | 35206 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 51 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8986 | 35207 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 52 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8987 | 35208 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 52 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8988 | 35209 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 52 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8989 | 35210 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 52 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x898A | 35211 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 53 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x898B | 35212 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 53 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x898C | 35213 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 53 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x898D | 35214 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 53 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x898E | 35215 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 54 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x898F | 35216 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 54 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8990 | 35217 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 54 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8991 | 35218 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 54 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8992 | 35219 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 55 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8993 | 35220 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 55 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8994 | 35221 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 55 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8995 | 35222 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 55 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8996 | 35223 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 56 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8997 | 35224 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 56 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8998 | 35225 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 56 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8999 | 35226 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 56 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x899A | 35227 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 57 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x899B | 35228 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 57 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x899C | 35229 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 57 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x899D | 35230 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 57 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x899E | 35231 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 58 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x899F | 35232 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 58 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89A0 | 35233 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 58 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89A1 | 35234 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 58 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89A2 | 35235 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 59 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89A3 | 35236 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 59 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89A4 | 35237 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 59 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89A5 | 35238 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 59 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89A6 | 35239 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 60 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89A7 | 35240 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 60 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89A8 | 35241 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 60 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89A9 | 35242 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 60 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89AA | 35243 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 61 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89AB | 35244 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 61 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89AC | 35245 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 61 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89AD | 35246 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 61 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89AE | 35247 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 62 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89AF | 35248 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 62 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89B0 | 35249 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 62 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89B1 | 35250 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 62 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89B2 | 35251 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 63 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89B3 | 35252 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 63 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89B4 | 35253 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 63 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89B5 | 35254 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 63 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89B6 | 35255 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 64 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89B7 | 35256 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 64 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89B8 | 35257 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 64 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89B9 | 35258 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 64 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89BA | 35259 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 65 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89BB | 35260 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 65 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89BC | 35261 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 65 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89BD | 35262 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 65 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89BE | 35263 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 66 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89BF | 35264 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 66 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89C0 | 35265 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 66 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89C1 | 35266 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 66 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89C2 | 35267 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 67 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89C3 | 35268 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 67 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89C4 | 35269 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 67 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89C5 | 35270 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 67 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89C6 | 35271 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 68 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89C7 | 35272 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 68 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89C8 | 35273 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 68 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89C9 | 35274 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 68 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89CA | 35275 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 69 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89CB | 35276 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 69 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89CC | 35277 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 69 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89CD | 35278 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 69 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89CE | 35279 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 70 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89CF | 35280 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 70 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89D0 | 35281 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 70 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89D1 | 35282 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 70 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89D2 | 35283 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 71 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89D3 | 35284 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 71 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89D4 | 35285 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 71 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89D5 | 35286 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 71 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89D6 | 35287 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 72 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89D7 | 35288 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 72 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89D8 | 35289 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 72 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89D9 | 35290 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 72 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89DA | 35291 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 73 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89DB | 35292 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 73 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89DC | 35293 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 73 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89DD | 35294 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 73 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89DE | 35295 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 74 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89DF | 35296 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 74 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89E0 | 35297 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 74 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89E1 | 35298 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 74 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89E2 | 35299 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 75 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89E3 | 35300 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 75 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89E4 | 35301 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 75 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89E5 | 35302 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 75 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89E6 | 35303 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 76 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89E7 | 35304 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 76 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89E8 | 35305 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 76 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89E9 | 35306 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 76 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89EA | 35307 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 77 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89EB | 35308 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 77 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89EC | 35309 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 77 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89ED | 35310 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 77 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89EE | 35311 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 78 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89EF | 35312 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 78 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89F0 | 35313 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 78 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89F1 | 35314 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 78 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89F2 | 35315 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 79 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89F3 | 35316 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 79 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89F4 | 35317 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 79 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89F5 | 35318 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 79 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89F6 | 35319 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 80 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89F7 | 35320 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 80 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89F8 | 35321 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 80 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89F9 | 35322 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 80 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89FA | 35323 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 81 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89FB | 35324 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 81 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89FC | 35325 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 81 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89FD | 35326 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 81 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89FE | 35327 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 82 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x89FF | 35328 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 82 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A00 | 35329 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 82 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A01 | 35330 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 82 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A02 | 35331 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 83 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A03 | 35332 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 83 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A04 | 35333 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 83 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A05 | 35334 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 83 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A06 | 35335 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 84 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A07 | 35336 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 84 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A08 | 35337 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 84 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A09 | 35338 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 84 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A0A | 35339 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 85 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A0B | 35340 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 85 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A0C | 35341 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 85 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A0D | 35342 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 85 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A0E | 35343 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 86 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A0F | 35344 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 86 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A10 | 35345 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 86 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A11 | 35346 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 86 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A12 | 35347 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 87 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A13 | 35348 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 87 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A14 | 35349 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 87 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A15 | 35350 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 87 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A16 | 35351 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 88 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A17 | 35352 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 88 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A18 | 35353 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 88 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A19 | 35354 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 88 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A1A | 35355 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 89 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A1B | 35356 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 89 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A1C | 35357 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 89 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A1D | 35358 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 89 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A1E | 35359 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 90 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A1F | 35360 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 90 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A20 | 35361 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 90 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A21 | 35362 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 90 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A22 | 35363 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 91 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A23 | 35364 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 91 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A24 | 35365 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 91 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A25 | 35366 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 91 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A26 | 35367 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 92 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A27 | 35368 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 92 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A28 | 35369 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 92 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A29 | 35370 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 92 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A2A | 35371 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 93 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A2B | 35372 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 93 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A2C | 35373 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 93 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A2D | 35374 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 93 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A2E | 35375 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 94 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A2F | 35376 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 94 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A30 | 35377 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 94 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A31 | 35378 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 94 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A32 | 35379 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 95 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A33 | 35380 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 95 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A34 | 35381 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 95 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A35 | 35382 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 95 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A36 | 35383 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 96 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A37 | 35384 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 96 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A38 | 35385 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 96 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A39 | 35386 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 96 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A3A | 35387 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 97 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A3B | 35388 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 97 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A3C | 35389 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 97 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A3D | 35390 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 97 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A3E | 35391 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 98 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A3F | 35392 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 98 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A40 | 35393 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 98 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A41 | 35394 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 98 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A42 | 35395 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 99 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A43 | 35396 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 99 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A44 | 35397 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 99 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A45 | 35398 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 99 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A46 | 35399 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 100 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A47 | 35400 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 100 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A48 | 35401 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 100 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A49 | 35402 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 100 • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active | x | x | x |  | x | x | x | x | x | x |  |  |  | x | x
Load Monitoring - Alarm | 0x8A4A | 35403 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 1 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A4B | 35404 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 1 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A4C | 35405 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 2 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A4D | 35406 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 2 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A4E | 35407 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 3 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A4F | 35408 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 3 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A50 | 35409 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 4 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A51 | 35410 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 4 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A52 | 35411 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 5 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A53 | 35412 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 5 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A54 | 35413 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 6 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A55 | 35414 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 6 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A56 | 35415 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 7 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A57 | 35416 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 7 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A58 | 35417 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 8 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A59 | 35418 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 8 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A5A | 35419 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 9 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A5B | 35420 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 9 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A5C | 35421 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 10 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A5D | 35422 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 10 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A5E | 35423 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 11 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A5F | 35424 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 11 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A60 | 35425 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 12 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A61 | 35426 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 12 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A62 | 35427 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 13 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A63 | 35428 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 13 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A64 | 35429 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 14 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A65 | 35430 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 14 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A66 | 35431 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 15 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A67 | 35432 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 15 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A68 | 35433 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 16 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A69 | 35434 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 16 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A6A | 35435 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 17 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A6B | 35436 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 17 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A6C | 35437 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 18 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A6D | 35438 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 18 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A6E | 35439 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 19 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A6F | 35440 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 19 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A70 | 35441 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 20 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A71 | 35442 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 20 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A72 | 35443 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 21 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A73 | 35444 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 21 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A74 | 35445 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 22 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A75 | 35446 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 22 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A76 | 35447 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 23 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A77 | 35448 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 23 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A78 | 35449 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 24 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A79 | 35450 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 24 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A7A | 35451 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 25 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A7B | 35452 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 25 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A7C | 35453 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 26 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A7D | 35454 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 26 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A7E | 35455 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 27 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A7F | 35456 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 27 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A80 | 35457 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 28 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A81 | 35458 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 28 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A82 | 35459 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 29 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A83 | 35460 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 29 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A84 | 35461 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 30 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A85 | 35462 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 30 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A86 | 35463 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 31 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A87 | 35464 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 31 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A88 | 35465 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 32 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A89 | 35466 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 32 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A8A | 35467 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 33 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A8B | 35468 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 33 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A8C | 35469 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 34 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A8D | 35470 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 34 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A8E | 35471 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 35 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A8F | 35472 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 35 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A90 | 35473 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 36 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A91 | 35474 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 36 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A92 | 35475 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 37 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A93 | 35476 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 37 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A94 | 35477 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 38 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A95 | 35478 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 38 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A96 | 35479 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 39 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A97 | 35480 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 39 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A98 | 35481 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 40 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A99 | 35482 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 40 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A9A | 35483 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 41 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A9B | 35484 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 41 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A9C | 35485 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 42 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A9D | 35486 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 42 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A9E | 35487 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 43 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8A9F | 35488 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 43 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AA0 | 35489 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 44 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AA1 | 35490 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 44 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AA2 | 35491 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 45 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AA3 | 35492 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 45 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AA4 | 35493 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 46 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AA5 | 35494 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 46 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AA6 | 35495 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 47 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AA7 | 35496 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 47 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AA8 | 35497 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 48 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AA9 | 35498 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 48 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AAA | 35499 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 49 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AAB | 35500 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 49 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AAC | 35501 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 50 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AAD | 35502 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 50 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AAE | 35503 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 51 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AAF | 35504 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 51 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AB0 | 35505 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 52 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AB1 | 35506 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 52 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AB2 | 35507 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 53 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AB3 | 35508 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 53 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AB4 | 35509 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 54 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AB5 | 35510 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 54 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AB6 | 35511 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 55 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AB7 | 35512 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 55 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AB8 | 35513 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 56 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AB9 | 35514 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 56 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8ABA | 35515 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 57 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8ABB | 35516 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 57 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8ABC | 35517 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 58 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8ABD | 35518 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 58 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8ABE | 35519 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 59 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8ABF | 35520 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 59 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AC0 | 35521 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 60 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AC1 | 35522 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 60 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AC2 | 35523 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 61 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AC3 | 35524 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 61 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AC4 | 35525 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 62 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AC5 | 35526 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 62 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AC6 | 35527 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 63 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AC7 | 35528 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 63 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AC8 | 35529 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 64 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AC9 | 35530 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 64 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8ACA | 35531 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 65 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8ACB | 35532 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 65 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8ACC | 35533 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 66 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8ACD | 35534 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 66 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8ACE | 35535 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 67 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8ACF | 35536 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 67 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AD0 | 35537 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 68 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AD1 | 35538 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 68 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AD2 | 35539 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 69 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AD3 | 35540 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 69 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AD4 | 35541 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 70 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AD5 | 35542 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 70 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AD6 | 35543 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 71 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AD7 | 35544 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 71 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AD8 | 35545 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 72 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AD9 | 35546 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 72 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8ADA | 35547 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 73 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8ADB | 35548 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 73 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8ADC | 35549 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 74 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8ADD | 35550 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 74 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8ADE | 35551 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 75 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8ADF | 35552 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 75 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AE0 | 35553 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 76 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AE1 | 35554 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 76 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AE2 | 35555 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 77 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AE3 | 35556 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 77 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AE4 | 35557 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 78 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AE5 | 35558 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 78 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AE6 | 35559 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 79 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AE7 | 35560 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 79 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AE8 | 35561 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 80 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AE9 | 35562 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 80 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AEA | 35563 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 81 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AEB | 35564 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 81 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AEC | 35565 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 82 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AED | 35566 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 82 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AEE | 35567 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 83 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AEF | 35568 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 83 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AF0 | 35569 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 84 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AF1 | 35570 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 84 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AF2 | 35571 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 85 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AF3 | 35572 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 85 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AF4 | 35573 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 86 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AF5 | 35574 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 86 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AF6 | 35575 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 87 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AF7 | 35576 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 87 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AF8 | 35577 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 88 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AF9 | 35578 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 88 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AFA | 35579 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 89 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AFB | 35580 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 89 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AFC | 35581 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 90 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AFD | 35582 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 90 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AFE | 35583 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 91 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8AFF | 35584 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 91 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8B00 | 35585 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 92 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8B01 | 35586 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 92 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8B02 | 35587 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 93 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8B03 | 35588 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 93 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8B04 | 35589 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 94 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8B05 | 35590 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 94 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8B06 | 35591 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 95 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8B07 | 35592 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 95 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8B08 | 35593 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 96 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8B09 | 35594 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 96 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8B0A | 35595 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 97 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8B0B | 35596 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 97 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8B0C | 35597 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 98 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8B0D | 35598 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 98 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8B0E | 35599 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 99 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8B0F | 35600 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 99 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8B10 | 35601 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 100 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
Load Monitoring - Alarm | 0x8B11 | 35602 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) of wireless device 100 • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm | [8 empty] | x |  |  |  |  | x | x
HeatTag Sensor | 0x8B12 | 35603 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 1 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B13 | 35604 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 2 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B14 | 35605 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 3 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B15 | 35606 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 4 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B16 | 35607 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 5 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B17 | 35608 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 6 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B18 | 35609 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 7 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B19 | 35610 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 8 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B1A | 35611 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 9 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B1B | 35612 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 10 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B1C | 35613 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 11 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B1D | 35614 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 12 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B1E | 35615 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 13 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B1F | 35616 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 14 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B20 | 35617 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 15 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B21 | 35618 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 16 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B22 | 35619 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 17 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B23 | 35620 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 18 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B24 | 35621 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 19 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B25 | 35622 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 20 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B26 | 35623 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 21 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B27 | 35624 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 22 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B28 | 35625 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 23 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B29 | 35626 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 24 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B2A | 35627 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 25 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B2B | 35628 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 26 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B2C | 35629 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 27 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B2D | 35630 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 28 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B2E | 35631 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 29 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B2F | 35632 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 30 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B30 | 35633 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 31 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B31 | 35634 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 32 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B32 | 35635 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 33 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B33 | 35636 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 34 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B34 | 35637 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 35 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B35 | 35638 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 36 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B36 | 35639 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 37 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B37 | 35640 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 38 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B38 | 35641 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 39 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B39 | 35642 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 40 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B3A | 35643 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 41 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B3B | 35644 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 42 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B3C | 35645 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 43 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B3D | 35646 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 44 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B3E | 35647 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 45 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B3F | 35648 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 46 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B40 | 35649 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 47 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B41 | 35650 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 48 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B42 | 35651 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 49 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B43 | 35652 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 50 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B44 | 35653 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 51 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B45 | 35654 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 52 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B46 | 35655 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 53 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B47 | 35656 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 54 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B48 | 35657 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 55 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B49 | 35658 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 56 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B4A | 35659 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 57 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B4B | 35660 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 58 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B4C | 35661 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 59 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B4D | 35662 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 60 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B4E | 35663 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 61 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B4F | 35664 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 62 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B50 | 35665 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 63 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B51 | 35666 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 64 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B52 | 35667 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 65 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B53 | 35668 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 66 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B54 | 35669 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 67 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B55 | 35670 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 68 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B56 | 35671 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 69 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B57 | 35672 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 70 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B58 | 35673 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 71 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B59 | 35674 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 72 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B5A | 35675 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 73 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B5B | 35676 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 74 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B5C | 35677 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 75 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B5D | 35678 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 76 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B5E | 35679 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 77 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B5F | 35680 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 78 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B60 | 35681 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 79 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B61 | 35682 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 80 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B62 | 35683 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 81 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B63 | 35684 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 82 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B64 | 35685 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 83 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B65 | 35686 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 84 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B66 | 35687 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 85 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B67 | 35688 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 86 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B68 | 35689 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 87 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B69 | 35690 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 88 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B6A | 35691 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 89 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B6B | 35692 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 90 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B6C | 35693 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 91 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B6D | 35694 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 92 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B6E | 35695 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 93 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B6F | 35696 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 94 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B70 | 35697 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 95 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B71 | 35698 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 96 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B72 | 35699 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 97 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B73 | 35700 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 98 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B74 | 35701 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 99 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B75 | 35702 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm type of wireless device 100 • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide) | [7 empty] | x
HeatTag Sensor | 0x8B76 | 35703 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 1 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B77 | 35704 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 2 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B78 | 35705 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 3 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B79 | 35706 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 4 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B7A | 35707 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 5 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B7B | 35708 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 6 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B7C | 35709 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 7 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B7D | 35710 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 8 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B7E | 35711 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 9 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B7F | 35712 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 10 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B80 | 35713 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 11 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B81 | 35714 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 12 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B82 | 35715 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 13 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B83 | 35716 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 14 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B84 | 35717 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 15 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B85 | 35718 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 16 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B86 | 35719 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 17 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B87 | 35720 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 18 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B88 | 35721 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 19 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B89 | 35722 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 20 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B8A | 35723 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 21 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B8B | 35724 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 22 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B8C | 35725 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 23 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B8D | 35726 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 24 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B8E | 35727 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 25 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B8F | 35728 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 26 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B90 | 35729 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 27 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B91 | 35730 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 28 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B92 | 35731 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 29 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B93 | 35732 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 30 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B94 | 35733 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 31 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B95 | 35734 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 32 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B96 | 35735 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 33 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B97 | 35736 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 34 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B98 | 35737 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 35 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B99 | 35738 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 36 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B9A | 35739 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 37 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B9B | 35740 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 38 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B9C | 35741 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 39 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B9D | 35742 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 40 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B9E | 35743 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 41 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8B9F | 35744 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 42 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BA0 | 35745 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 43 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BA1 | 35746 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 44 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BA2 | 35747 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 45 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BA3 | 35748 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 46 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BA4 | 35749 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 47 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BA5 | 35750 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 48 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BA6 | 35751 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 49 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BA7 | 35752 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 50 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BA8 | 35753 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 51 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BA9 | 35754 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 52 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BAA | 35755 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 53 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BAB | 35756 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 54 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BAC | 35757 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 55 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BAD | 35758 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 56 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BAE | 35759 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 57 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BAF | 35760 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 58 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BB0 | 35761 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 59 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BB1 | 35762 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 60 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BB2 | 35763 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 61 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BB3 | 35764 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 62 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BB4 | 35765 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 63 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BB5 | 35766 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 64 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BB6 | 35767 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 65 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BB7 | 35768 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 66 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BB8 | 35769 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 67 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BB9 | 35770 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 68 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BBA | 35771 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 69 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BBB | 35772 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 70 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BBC | 35773 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 71 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BBD | 35774 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 72 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BBE | 35775 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 73 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BBF | 35776 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 74 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BC0 | 35777 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 75 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BC1 | 35778 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 76 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BC2 | 35779 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 77 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BC3 | 35780 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 78 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BC4 | 35781 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 79 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BC5 | 35782 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 80 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BC6 | 35783 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 81 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BC7 | 35784 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 82 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BC8 | 35785 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 83 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BC9 | 35786 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 84 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BCA | 35787 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 85 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BCB | 35788 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 86 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BCC | 35789 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 87 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BCD | 35790 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 88 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BCE | 35791 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 89 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BCF | 35792 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 90 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BD0 | 35793 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 91 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BD1 | 35794 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 92 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BD2 | 35795 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 93 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BD3 | 35796 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 94 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BD4 | 35797 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 95 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BD5 | 35798 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 96 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BD6 | 35799 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 97 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BD7 | 35800 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 98 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BD8 | 35801 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 99 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
HeatTag Sensor | 0x8BD9 | 35802 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | HeatTag alarm level of wireless device 100 • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm | [7 empty] | x
Load Monitoring - Alarm | 0x8BDA | 35803 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 1 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BDB | 35804 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 1 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BDC | 35805 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 2 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BDD | 35806 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 2 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BDE | 35807 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 3 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BDF | 35808 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 3 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BE0 | 35809 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 4 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BE1 | 35810 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 4 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BE2 | 35811 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 5 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BE3 | 35812 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 5 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BE4 | 35813 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 6 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BE5 | 35814 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 6 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BE6 | 35815 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 7 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BE7 | 35816 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 7 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BE8 | 35817 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 8 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BE9 | 35818 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 8 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BEA | 35819 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 9 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BEB | 35820 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 9 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BEC | 35821 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 10 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BED | 35822 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 10 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BEE | 35823 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 11 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BEF | 35824 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 11 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BF0 | 35825 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 12 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BF1 | 35826 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 12 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BF2 | 35827 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 13 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BF3 | 35828 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 13 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BF4 | 35829 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 14 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BF5 | 35830 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 14 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BF6 | 35831 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 15 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BF7 | 35832 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 15 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BF8 | 35833 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 16 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BF9 | 35834 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 16 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BFA | 35835 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 17 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BFB | 35836 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 17 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BFC | 35837 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 18 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BFD | 35838 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 18 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BFE | 35839 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 19 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8BFF | 35840 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 19 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C00 | 35841 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 20 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C01 | 35842 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 20 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C02 | 35843 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 21 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C03 | 35844 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 21 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C04 | 35845 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 22 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C05 | 35846 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 22 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C06 | 35847 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 23 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C07 | 35848 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 23 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C08 | 35849 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 24 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C09 | 35850 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 24 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C0A | 35851 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 25 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C0B | 35852 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 25 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C0C | 35853 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 26 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C0D | 35854 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 26 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C0E | 35855 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 27 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C0F | 35856 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 27 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C10 | 35857 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 28 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C11 | 35858 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 28 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C12 | 35859 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 29 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C13 | 35860 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 29 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C14 | 35861 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 30 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C15 | 35862 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 30 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C16 | 35863 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 31 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C17 | 35864 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 31 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C18 | 35865 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 32 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C19 | 35866 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 32 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C1A | 35867 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 33 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C1B | 35868 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 33 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C1C | 35869 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 34 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C1D | 35870 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 34 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C1E | 35871 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 35 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C1F | 35872 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 35 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C20 | 35873 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 36 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C21 | 35874 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 36 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C22 | 35875 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 37 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C23 | 35876 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 37 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C24 | 35877 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 38 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C25 | 35878 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 38 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C26 | 35879 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 39 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C27 | 35880 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 39 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C28 | 35881 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 40 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C29 | 35882 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 40 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C2A | 35883 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 41 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C2B | 35884 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 41 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C2C | 35885 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 42 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C2D | 35886 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 42 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C2E | 35887 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 43 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C2F | 35888 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 43 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C30 | 35889 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 44 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C31 | 35890 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 44 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C32 | 35891 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 45 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C33 | 35892 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 45 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C34 | 35893 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 46 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C35 | 35894 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 46 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C36 | 35895 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 47 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C37 | 35896 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 47 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C38 | 35897 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 48 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C39 | 35898 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 48 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C3A | 35899 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 49 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C3B | 35900 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 49 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C3C | 35901 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 50 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C3D | 35902 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 50 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C3E | 35903 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 51 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C3F | 35904 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 51 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C40 | 35905 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 52 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C41 | 35906 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 52 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C42 | 35907 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 53 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C43 | 35908 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 53 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C44 | 35909 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 54 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C45 | 35910 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 54 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C46 | 35911 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 55 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C47 | 35912 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 55 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C48 | 35913 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 56 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C49 | 35914 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 56 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C4A | 35915 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 57 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C4B | 35916 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 57 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C4C | 35917 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 58 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C4D | 35918 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 58 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C4E | 35919 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 59 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C4F | 35920 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 59 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C50 | 35921 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 60 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C51 | 35922 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 60 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C52 | 35923 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 61 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C53 | 35924 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 61 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C54 | 35925 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 62 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C55 | 35926 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 62 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C56 | 35927 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 63 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C57 | 35928 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 63 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C58 | 35929 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 64 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C59 | 35930 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 64 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C5A | 35931 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 65 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C5B | 35932 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 65 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C5C | 35933 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 66 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C5D | 35934 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 66 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C5E | 35935 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 67 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C5F | 35936 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 67 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C60 | 35937 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 68 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C61 | 35938 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 68 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C62 | 35939 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 69 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C63 | 35940 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 69 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C64 | 35941 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 70 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C65 | 35942 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 70 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C66 | 35943 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 71 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C67 | 35944 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 71 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C68 | 35945 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 72 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C69 | 35946 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 72 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C6A | 35947 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 73 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C6B | 35948 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 73 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C6C | 35949 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 74 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C6D | 35950 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 74 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C6E | 35951 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 75 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C6F | 35952 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 75 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C70 | 35953 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 76 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C71 | 35954 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 76 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C72 | 35955 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 77 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C73 | 35956 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 77 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C74 | 35957 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 78 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C75 | 35958 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 78 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C76 | 35959 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 79 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C77 | 35960 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 79 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C78 | 35961 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 80 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C79 | 35962 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 80 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C7A | 35963 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 81 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C7B | 35964 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 81 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C7C | 35965 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 82 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C7D | 35966 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 82 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C7E | 35967 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 83 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C7F | 35968 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 83 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C80 | 35969 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 84 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C81 | 35970 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 84 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C82 | 35971 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 85 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C83 | 35972 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 85 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C84 | 35973 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 86 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C85 | 35974 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 86 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C86 | 35975 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 87 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C87 | 35976 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 87 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C88 | 35977 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 88 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C89 | 35978 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 88 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C8A | 35979 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 89 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C8B | 35980 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 89 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C8C | 35981 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 90 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C8D | 35982 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 90 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C8E | 35983 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 91 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C8F | 35984 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 91 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C90 | 35985 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 92 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C91 | 35986 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 92 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C92 | 35987 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 93 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C93 | 35988 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 93 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C94 | 35989 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 94 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C95 | 35990 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 94 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C96 | 35991 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 95 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C97 | 35992 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 95 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C98 | 35993 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 96 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C99 | 35994 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 96 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C9A | 35995 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 97 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C9B | 35996 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 97 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C9C | 35997 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 98 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C9D | 35998 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 98 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C9E | 35999 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 99 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8C9F | 36000 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 99 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8CA0 | 36001 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) of wireless device 100 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm | [14 empty] | x
Load Monitoring - Alarm | 0x8CA1 | 36002 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | State of the alarm bitmap (0 = Inactive / 1 = Active) of wireless device 100 • Bit 0 = Long-time protection alarm • Bit 1 = Short-time protection alarm • Bit 4 = Earth-leakage protection alarm • Bit 7 = AAF protection (Serial) alarm • Bit 8 = AAF protection (Parallel) alarm • Bit 12 = Push-button test alarm • Bit 13 = Internal cause alarm • Bit 14 = Tripping chain failure alarm | [14 empty] | x
Diagnostic Data | 0x9C40 | 40001 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 1 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C41 | 40002 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 1. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C42 | 40003 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 2 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C43 | 40004 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 2. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C44 | 40005 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 3 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C45 | 40006 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 3. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C46 | 40007 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 4 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C47 | 40008 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 4. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C48 | 40009 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 5 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C49 | 40010 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 5. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C4A | 40011 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 6 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C4B | 40012 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 6. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C4C | 40013 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 7 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C4D | 40014 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 7. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C4E | 40015 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 8 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C4F | 40016 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 8. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C50 | 40017 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 9 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C51 | 40018 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 9. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C52 | 40019 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 10 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C53 | 40020 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 10. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C54 | 40021 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 11 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C55 | 40022 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 11. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C56 | 40023 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 12 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C57 | 40024 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 12. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C58 | 40025 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 13 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C59 | 40026 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 13. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C5A | 40027 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 14 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C5B | 40028 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 14. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C5C | 40029 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 15 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C5D | 40030 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 15. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C5E | 40031 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 16 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C5F | 40032 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 16. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C60 | 40033 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 17 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C61 | 40034 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 17. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C62 | 40035 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 18 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C63 | 40036 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 18. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C64 | 40037 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 19 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C65 | 40038 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 19. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C66 | 40039 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 20 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C67 | 40040 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 20. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C68 | 40041 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 21 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C69 | 40042 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 21. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C6A | 40043 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 22 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C6B | 40044 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 22. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C6C | 40045 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 23 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C6D | 40046 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 23. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C6E | 40047 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 24 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C6F | 40048 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 24. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C70 | 40049 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 25 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C71 | 40050 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 25. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C72 | 40051 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 26 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C73 | 40052 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 26. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C74 | 40053 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 27 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C75 | 40054 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 27. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C76 | 40055 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 28 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C77 | 40056 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 28. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C78 | 40057 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 29 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C79 | 40058 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 29. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C7A | 40059 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 30 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C7B | 40060 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 30. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C7C | 40061 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 31 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C7D | 40062 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 31. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C7E | 40063 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 32 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C7F | 40064 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 32. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C80 | 40065 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 33 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C81 | 40066 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 33. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C82 | 40067 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 34 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C83 | 40068 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 34. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C84 | 40069 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 35 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C85 | 40070 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 35. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C86 | 40071 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 36 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C87 | 40072 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 36. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C88 | 40073 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 37 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C89 | 40074 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 37. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C8A | 40075 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 38 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C8B | 40076 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 38. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C8C | 40077 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 39 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C8D | 40078 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 39. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C8E | 40079 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 40 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C8F | 40080 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 40. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C90 | 40081 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 41 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C91 | 40082 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 41. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C92 | 40083 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 42 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C93 | 40084 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 42. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C94 | 40085 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 43 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C95 | 40086 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 43. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C96 | 40087 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 44 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C97 | 40088 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 44. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C98 | 40089 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 45 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C99 | 40090 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 45. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C9A | 40091 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 46 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C9B | 40092 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 46. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C9C | 40093 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 47 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C9D | 40094 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 47. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C9E | 40095 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 48 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9C9F | 40096 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 48. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CA0 | 40097 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 49 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CA1 | 40098 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 49. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CA2 | 40099 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 50 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CA3 | 40100 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 50. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CA4 | 40101 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 51 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CA5 | 40102 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 51. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CA6 | 40103 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 52 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CA7 | 40104 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 52. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CA8 | 40105 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 53 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CA9 | 40106 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 53. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CAA | 40107 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 54 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CAB | 40108 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 54. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CAC | 40109 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 55 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CAD | 40110 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 55. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CAE | 40111 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 56 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CAF | 40112 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 56. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CB0 | 40113 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 57 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CB1 | 40114 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 57. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CB2 | 40115 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 58 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CB3 | 40116 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 58. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CB4 | 40117 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 59 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CB5 | 40118 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 59. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CB6 | 40119 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 60 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CB7 | 40120 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 60. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CB8 | 40121 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 61 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CB9 | 40122 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 61. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CBA | 40123 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 62 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CBB | 40124 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 62. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CBC | 40125 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 63 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CBD | 40126 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 63. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CBE | 40127 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 64 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CBF | 40128 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 64. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CC0 | 40129 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 65 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CC1 | 40130 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 65. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CC2 | 40131 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 66 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CC3 | 40132 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 66. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CC4 | 40133 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 67 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CC5 | 40134 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 67. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CC6 | 40135 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 68 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CC7 | 40136 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 68. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CC8 | 40137 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 69 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CC9 | 40138 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 69. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CCA | 40139 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 70 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CCB | 40140 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 70. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CCC | 40141 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 71 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CCD | 40142 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 71. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CCE | 40143 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 72 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CCF | 40144 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 72. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CD0 | 40145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 73 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CD1 | 40146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 73. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CD2 | 40147 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 74 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CD3 | 40148 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 74. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CD4 | 40149 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 75 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CD5 | 40150 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 75. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CD6 | 40151 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 76 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CD7 | 40152 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 76. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CD8 | 40153 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 77 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CD9 | 40154 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 77. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CDA | 40155 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 78 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CDB | 40156 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 78. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CDC | 40157 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 79 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CDD | 40158 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 79. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CDE | 40159 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 80 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CDF | 40160 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 80. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CE0 | 40161 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 81 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CE1 | 40162 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 81. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CE2 | 40163 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 82 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CE3 | 40164 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 82. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CE4 | 40165 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 83 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CE5 | 40166 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 83. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CE6 | 40167 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 84 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CE7 | 40168 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 84. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CE8 | 40169 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 85 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CE9 | 40170 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 85. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CEA | 40171 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 86 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CEB | 40172 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 86. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CEC | 40173 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 87 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CED | 40174 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 87. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CEE | 40175 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 88 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CEF | 40176 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 88. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CF0 | 40177 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 89 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CF1 | 40178 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 89. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CF2 | 40179 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 90 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CF3 | 40180 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 90. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CF4 | 40181 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 91 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CF5 | 40182 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 91. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CF6 | 40183 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 92 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CF7 | 40184 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 92. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CF8 | 40185 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 93 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CF9 | 40186 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 93. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CFA | 40187 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 94 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CFB | 40188 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 94. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CFC | 40189 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 95 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CFD | 40190 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 95. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CFE | 40191 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 96 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9CFF | 40192 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 96. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9D00 | 40193 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 97 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9D01 | 40194 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 97. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9D02 | 40195 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 98 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9D03 | 40196 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 98. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9D04 | 40197 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 99 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9D05 | 40198 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 99. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9D06 | 40199 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the wireless device 100 and Panel Server status. • 0 = Invalid • 1 = Valid | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Diagnostic Data | 0x9D07 | 40200 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless device 100. • 0 = Communication loss • 1 = Communication OK | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Digital input | 0xAFC8 | 45001 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 1 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFC9 | 45002 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 2 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFCA | 45003 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 3 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFCB | 45004 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 4 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFCC | 45005 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 5 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFCD | 45006 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 6 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFCE | 45007 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 7 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFCF | 45008 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 8 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFD0 | 45009 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 9 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFD1 | 45010 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 10 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFD2 | 45011 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 11 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFD3 | 45012 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 12 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFD4 | 45013 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 13 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFD5 | 45014 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 14 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFD6 | 45015 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 15 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFD7 | 45016 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 16 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFD8 | 45017 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 17 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFD9 | 45018 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 18 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFDA | 45019 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 19 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFDB | 45020 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 20 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFDC | 45021 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 21 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFDD | 45022 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 22 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFDE | 45023 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 23 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFDF | 45024 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 24 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFE0 | 45025 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 25 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFE1 | 45026 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 26 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFE2 | 45027 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 27 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFE3 | 45028 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 28 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFE4 | 45029 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 29 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFE5 | 45030 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 30 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFE6 | 45031 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 31 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFE7 | 45032 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 32 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFE8 | 45033 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 33 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFE9 | 45034 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 34 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFEA | 45035 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 35 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFEB | 45036 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 36 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFEC | 45037 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 37 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFED | 45038 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 38 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFEE | 45039 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 39 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFEF | 45040 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 40 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFF0 | 45041 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 41 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFF1 | 45042 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 42 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFF2 | 45043 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 43 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFF3 | 45044 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 44 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFF4 | 45045 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 45 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFF5 | 45046 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 46 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFF6 | 45047 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 47 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFF7 | 45048 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 48 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFF8 | 45049 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 49 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFF9 | 45050 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 50 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFFA | 45051 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 51 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFFB | 45052 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 52 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFFC | 45053 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 53 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFFD | 45054 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 54 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFFE | 45055 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 55 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xAFFF | 45056 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 56 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB000 | 45057 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 57 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB001 | 45058 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 58 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB002 | 45059 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 59 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB003 | 45060 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 60 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB004 | 45061 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 61 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB005 | 45062 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 62 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB006 | 45063 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 63 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB007 | 45064 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 64 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB008 | 45065 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 65 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB009 | 45066 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 66 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB00A | 45067 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 67 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB00B | 45068 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 68 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB00C | 45069 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 69 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB00D | 45070 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 70 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB00E | 45071 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 71 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB00F | 45072 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 72 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB010 | 45073 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 73 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB011 | 45074 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 74 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB012 | 45075 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 75 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB013 | 45076 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 76 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB014 | 45077 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 77 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB015 | 45078 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 78 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB016 | 45079 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 79 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB017 | 45080 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 80 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB018 | 45081 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 81 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB019 | 45082 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 82 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB01A | 45083 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 83 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB01B | 45084 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 84 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB01C | 45085 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 85 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB01D | 45086 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 86 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB01E | 45087 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 87 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB01F | 45088 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 88 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB020 | 45089 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 89 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB021 | 45090 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 90 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB022 | 45091 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 91 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB023 | 45092 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 92 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB024 | 45093 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 93 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB025 | 45094 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 94 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB026 | 45095 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 95 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB027 | 45096 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 96 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB028 | 45097 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 97 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB029 | 45098 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 98 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB02A | 45099 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 99 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB02B | 45100 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 1 of wireless device 100 • 0 = Open • 1 = Closed | [11 empty] | x | x
Digital input | 0xB02C | 45101 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 1 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB02D | 45102 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 2 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB02E | 45103 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 3 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB02F | 45104 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 4 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB030 | 45105 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 5 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB031 | 45106 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 6 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB032 | 45107 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 7 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB033 | 45108 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 8 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB034 | 45109 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 9 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB035 | 45110 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 10 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB036 | 45111 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 11 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB037 | 45112 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 12 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB038 | 45113 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 13 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB039 | 45114 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 14 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB03A | 45115 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 15 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB03B | 45116 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 16 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB03C | 45117 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 17 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB03D | 45118 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 18 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB03E | 45119 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 19 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB03F | 45120 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 20 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB040 | 45121 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 21 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB041 | 45122 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 22 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB042 | 45123 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 23 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB043 | 45124 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 24 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB044 | 45125 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 25 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB045 | 45126 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 26 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB046 | 45127 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 27 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB047 | 45128 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 28 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB048 | 45129 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 29 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB049 | 45130 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 30 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB04A | 45131 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 31 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB04B | 45132 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 32 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB04C | 45133 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 33 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB04D | 45134 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 34 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB04E | 45135 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 35 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB04F | 45136 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 36 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB050 | 45137 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 37 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB051 | 45138 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 38 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB052 | 45139 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 39 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB053 | 45140 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 40 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB054 | 45141 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 41 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB055 | 45142 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 42 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB056 | 45143 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 43 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB057 | 45144 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 44 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB058 | 45145 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 45 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB059 | 45146 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 46 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB05A | 45147 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 47 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB05B | 45148 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 48 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB05C | 45149 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 49 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB05D | 45150 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 50 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB05E | 45151 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 51 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB05F | 45152 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 52 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB060 | 45153 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 53 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB061 | 45154 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 54 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB062 | 45155 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 55 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB063 | 45156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 56 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB064 | 45157 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 57 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB065 | 45158 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 58 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB066 | 45159 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 59 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB067 | 45160 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 60 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB068 | 45161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 61 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB069 | 45162 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 62 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB06A | 45163 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 63 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB06B | 45164 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 64 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB06C | 45165 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 65 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB06D | 45166 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 66 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB06E | 45167 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 67 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB06F | 45168 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 68 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB070 | 45169 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 69 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB071 | 45170 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 70 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB072 | 45171 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 71 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB073 | 45172 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 72 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB074 | 45173 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 73 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB075 | 45174 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 74 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB076 | 45175 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 75 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB077 | 45176 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 76 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB078 | 45177 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 77 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB079 | 45178 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 78 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB07A | 45179 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 79 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB07B | 45180 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 80 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB07C | 45181 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 81 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB07D | 45182 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 82 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB07E | 45183 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 83 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB07F | 45184 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 84 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB080 | 45185 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 85 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB081 | 45186 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 86 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB082 | 45187 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 87 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB083 | 45188 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 88 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB084 | 45189 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 89 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB085 | 45190 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 90 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB086 | 45191 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 91 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB087 | 45192 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 92 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB088 | 45193 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 93 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB089 | 45194 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 94 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB08A | 45195 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 95 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB08B | 45196 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 96 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB08C | 45197 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 97 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB08D | 45198 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 98 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB08E | 45199 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 99 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB08F | 45200 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 1 of wireless device 100 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x | x
Digital input | 0xB090 | 45201 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 1 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB091 | 45202 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 2 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB092 | 45203 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 3 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB093 | 45204 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 4 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB094 | 45205 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 5 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB095 | 45206 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 6 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB096 | 45207 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 7 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB097 | 45208 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 8 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB098 | 45209 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 9 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB099 | 45210 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 10 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB09A | 45211 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 11 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB09B | 45212 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 12 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB09C | 45213 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 13 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB09D | 45214 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 14 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB09E | 45215 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 15 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB09F | 45216 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 16 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0A0 | 45217 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 17 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0A1 | 45218 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 18 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0A2 | 45219 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 19 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0A3 | 45220 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 20 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0A4 | 45221 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 21 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0A5 | 45222 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 22 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0A6 | 45223 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 23 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0A7 | 45224 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 24 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0A8 | 45225 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 25 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0A9 | 45226 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 26 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0AA | 45227 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 27 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0AB | 45228 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 28 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0AC | 45229 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 29 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0AD | 45230 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 30 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0AE | 45231 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 31 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0AF | 45232 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 32 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0B0 | 45233 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 33 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0B1 | 45234 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 34 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0B2 | 45235 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 35 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0B3 | 45236 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 36 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0B4 | 45237 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 37 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0B5 | 45238 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 38 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0B6 | 45239 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 39 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0B7 | 45240 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 40 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0B8 | 45241 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 41 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0B9 | 45242 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 42 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0BA | 45243 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 43 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0BB | 45244 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 44 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0BC | 45245 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 45 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0BD | 45246 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 46 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0BE | 45247 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 47 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0BF | 45248 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 48 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0C0 | 45249 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 49 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0C1 | 45250 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 50 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0C2 | 45251 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 51 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0C3 | 45252 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 52 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0C4 | 45253 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 53 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0C5 | 45254 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 54 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0C6 | 45255 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 55 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0C7 | 45256 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 56 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0C8 | 45257 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 57 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0C9 | 45258 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 58 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0CA | 45259 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 59 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0CB | 45260 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 60 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0CC | 45261 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 61 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0CD | 45262 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 62 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0CE | 45263 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 63 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0CF | 45264 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 64 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0D0 | 45265 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 65 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0D1 | 45266 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 66 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0D2 | 45267 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 67 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0D3 | 45268 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 68 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0D4 | 45269 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 69 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0D5 | 45270 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 70 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0D6 | 45271 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 71 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0D7 | 45272 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 72 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0D8 | 45273 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 73 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0D9 | 45274 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 74 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0DA | 45275 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 75 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0DB | 45276 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 76 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0DC | 45277 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 77 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0DD | 45278 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 78 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0DE | 45279 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 79 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0DF | 45280 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 80 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0E0 | 45281 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 81 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0E1 | 45282 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 82 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0E2 | 45283 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 83 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0E3 | 45284 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 84 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0E4 | 45285 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 85 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0E5 | 45286 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 86 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0E6 | 45287 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 87 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0E7 | 45288 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 88 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0E8 | 45289 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 89 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0E9 | 45290 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 90 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0EA | 45291 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 91 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0EB | 45292 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 92 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0EC | 45293 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 93 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0ED | 45294 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 94 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0EE | 45295 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 95 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0EF | 45296 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 96 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0F0 | 45297 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 97 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0F1 | 45298 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 98 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0F2 | 45299 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 99 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0F3 | 45300 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 of wireless device 100 • 0 = OFF // Inactive • 1 = ON // Active | [9 empty] | x |  | x | x |  |  |  | x
Digital input | 0xB0F4 | 45301 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 1 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB0F5 | 45302 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 2 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB0F6 | 45303 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 3 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB0F7 | 45304 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 4 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB0F8 | 45305 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 5 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB0F9 | 45306 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 6 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB0FA | 45307 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 7 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB0FB | 45308 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 8 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB0FC | 45309 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 9 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB0FD | 45310 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 10 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB0FE | 45311 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 11 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB0FF | 45312 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 12 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB100 | 45313 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 13 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB101 | 45314 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 14 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB102 | 45315 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 15 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB103 | 45316 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 16 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB104 | 45317 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 17 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB105 | 45318 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 18 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB106 | 45319 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 19 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB107 | 45320 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 20 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB108 | 45321 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 21 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB109 | 45322 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 22 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB10A | 45323 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 23 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB10B | 45324 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 24 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB10C | 45325 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 25 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB10D | 45326 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 26 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB10E | 45327 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 27 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB10F | 45328 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 28 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB110 | 45329 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 29 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB111 | 45330 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 30 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB112 | 45331 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 31 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB113 | 45332 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 32 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB114 | 45333 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 33 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB115 | 45334 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 34 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB116 | 45335 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 35 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB117 | 45336 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 36 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB118 | 45337 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 37 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB119 | 45338 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 38 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB11A | 45339 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 39 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB11B | 45340 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 40 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB11C | 45341 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 41 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB11D | 45342 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 42 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB11E | 45343 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 43 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB11F | 45344 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 44 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB120 | 45345 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 45 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB121 | 45346 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 46 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB122 | 45347 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 47 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB123 | 45348 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 48 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB124 | 45349 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 49 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB125 | 45350 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 50 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB126 | 45351 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 51 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB127 | 45352 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 52 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB128 | 45353 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 53 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB129 | 45354 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 54 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB12A | 45355 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 55 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB12B | 45356 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 56 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB12C | 45357 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 57 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB12D | 45358 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 58 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB12E | 45359 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 59 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB12F | 45360 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 60 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB130 | 45361 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 61 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB131 | 45362 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 62 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB132 | 45363 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 63 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB133 | 45364 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 64 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB134 | 45365 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 65 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB135 | 45366 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 66 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB136 | 45367 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 67 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB137 | 45368 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 68 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB138 | 45369 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 69 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB139 | 45370 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 70 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB13A | 45371 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 71 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB13B | 45372 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 72 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB13C | 45373 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 73 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB13D | 45374 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 74 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB13E | 45375 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 75 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB13F | 45376 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 76 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB140 | 45377 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 77 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB141 | 45378 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 78 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB142 | 45379 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 79 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB143 | 45380 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 80 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB144 | 45381 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 81 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB145 | 45382 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 82 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB146 | 45383 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 83 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB147 | 45384 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 84 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB148 | 45385 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 85 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB149 | 45386 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 86 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB14A | 45387 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 87 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB14B | 45388 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 88 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB14C | 45389 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 89 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB14D | 45390 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 90 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB14E | 45391 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 91 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB14F | 45392 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 92 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB150 | 45393 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 93 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB151 | 45394 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 94 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB152 | 45395 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 95 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB153 | 45396 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 96 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB154 | 45397 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 97 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB155 | 45398 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 98 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB156 | 45399 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 99 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB157 | 45400 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position of the Digital Input 2 of wireless device 100 • 0 = Open • 1 = Closed | [11 empty] | x
Digital input | 0xB158 | 45401 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 1 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB159 | 45402 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 2 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB15A | 45403 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 3 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB15B | 45404 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 4 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB15C | 45405 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 5 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB15D | 45406 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 6 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB15E | 45407 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 7 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB15F | 45408 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 8 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB160 | 45409 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 9 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB161 | 45410 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 10 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB162 | 45411 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 11 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB163 | 45412 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 12 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB164 | 45413 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 13 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB165 | 45414 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 14 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB166 | 45415 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 15 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB167 | 45416 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 16 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB168 | 45417 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 17 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB169 | 45418 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 18 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB16A | 45419 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 19 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB16B | 45420 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 20 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB16C | 45421 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 21 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB16D | 45422 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 22 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB16E | 45423 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 23 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB16F | 45424 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 24 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB170 | 45425 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 25 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB171 | 45426 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 26 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB172 | 45427 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 27 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB173 | 45428 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 28 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB174 | 45429 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 29 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB175 | 45430 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 30 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB176 | 45431 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 31 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB177 | 45432 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 32 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB178 | 45433 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 33 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB179 | 45434 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 34 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB17A | 45435 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 35 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB17B | 45436 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 36 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB17C | 45437 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 37 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB17D | 45438 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 38 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB17E | 45439 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 39 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB17F | 45440 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 40 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB180 | 45441 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 41 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB181 | 45442 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 42 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB182 | 45443 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 43 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB183 | 45444 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 44 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB184 | 45445 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 45 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB185 | 45446 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 46 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB186 | 45447 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 47 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB187 | 45448 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 48 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB188 | 45449 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 49 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB189 | 45450 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 50 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB18A | 45451 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 51 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB18B | 45452 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 52 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB18C | 45453 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 53 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB18D | 45454 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 54 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB18E | 45455 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 55 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB18F | 45456 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 56 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB190 | 45457 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 57 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB191 | 45458 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 58 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB192 | 45459 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 59 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB193 | 45460 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 60 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB194 | 45461 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 61 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB195 | 45462 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 62 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB196 | 45463 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 63 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB197 | 45464 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 64 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB198 | 45465 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 65 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB199 | 45466 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 66 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB19A | 45467 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 67 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB19B | 45468 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 68 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB19C | 45469 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 69 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB19D | 45470 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 70 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB19E | 45471 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 71 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB19F | 45472 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 72 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB1A0 | 45473 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 73 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB1A1 | 45474 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 74 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB1A2 | 45475 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 75 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB1A3 | 45476 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 76 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB1A4 | 45477 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 77 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB1A5 | 45478 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 78 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB1A6 | 45479 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 79 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB1A7 | 45480 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 80 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB1A8 | 45481 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 81 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB1A9 | 45482 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 82 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB1AA | 45483 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 83 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB1AB | 45484 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 84 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB1AC | 45485 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 85 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB1AD | 45486 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 86 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB1AE | 45487 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 87 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB1AF | 45488 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 88 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB1B0 | 45489 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 89 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB1B1 | 45490 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 90 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB1B2 | 45491 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 91 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB1B3 | 45492 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 92 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB1B4 | 45493 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 93 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB1B5 | 45494 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 94 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB1B6 | 45495 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 95 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB1B7 | 45496 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 96 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB1B8 | 45497 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 97 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB1B9 | 45498 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 98 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB1BA | 45499 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 99 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB1BB | 45500 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip of the Digital Input 2 of wireless device 100 • 0 = ON // Tripped • 1 = OFF // Not tripped | [11 empty] | x
Digital input | 0xB1BC | 45501 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 1 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1BD | 45502 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 2 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1BE | 45503 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 3 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1BF | 45504 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 4 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1C0 | 45505 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 5 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1C1 | 45506 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 6 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1C2 | 45507 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 7 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1C3 | 45508 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 8 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1C4 | 45509 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 9 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1C5 | 45510 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 10 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1C6 | 45511 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 11 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1C7 | 45512 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 12 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1C8 | 45513 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 13 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1C9 | 45514 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 14 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1CA | 45515 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 15 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1CB | 45516 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 16 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1CC | 45517 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 17 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1CD | 45518 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 18 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1CE | 45519 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 19 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1CF | 45520 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 20 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1D0 | 45521 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 21 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1D1 | 45522 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 22 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1D2 | 45523 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 23 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1D3 | 45524 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 24 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1D4 | 45525 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 25 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1D5 | 45526 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 26 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1D6 | 45527 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 27 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1D7 | 45528 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 28 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1D8 | 45529 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 29 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1D9 | 45530 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 30 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1DA | 45531 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 31 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1DB | 45532 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 32 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1DC | 45533 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 33 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1DD | 45534 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 34 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1DE | 45535 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 35 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1DF | 45536 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 36 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1E0 | 45537 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 37 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1E1 | 45538 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 38 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1E2 | 45539 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 39 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1E3 | 45540 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 40 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1E4 | 45541 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 41 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1E5 | 45542 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 42 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1E6 | 45543 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 43 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1E7 | 45544 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 44 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1E8 | 45545 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 45 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1E9 | 45546 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 46 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1EA | 45547 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 47 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1EB | 45548 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 48 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1EC | 45549 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 49 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1ED | 45550 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 50 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1EE | 45551 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 51 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1EF | 45552 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 52 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1F0 | 45553 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 53 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1F1 | 45554 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 54 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1F2 | 45555 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 55 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1F3 | 45556 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 56 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1F4 | 45557 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 57 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1F5 | 45558 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 58 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1F6 | 45559 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 59 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1F7 | 45560 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 60 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1F8 | 45561 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 61 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1F9 | 45562 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 62 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1FA | 45563 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 63 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1FB | 45564 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 64 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1FC | 45565 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 65 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1FD | 45566 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 66 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1FE | 45567 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 67 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB1FF | 45568 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 68 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB200 | 45569 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 69 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB201 | 45570 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 70 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB202 | 45571 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 71 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB203 | 45572 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 72 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB204 | 45573 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 73 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB205 | 45574 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 74 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB206 | 45575 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 75 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB207 | 45576 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 76 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB208 | 45577 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 77 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB209 | 45578 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 78 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB20A | 45579 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 79 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB20B | 45580 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 80 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB20C | 45581 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 81 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB20D | 45582 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 82 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB20E | 45583 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 83 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB20F | 45584 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 84 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB210 | 45585 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 85 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB211 | 45586 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 86 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB212 | 45587 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 87 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB213 | 45588 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 88 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB214 | 45589 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 89 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB215 | 45590 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 90 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB216 | 45591 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 91 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB217 | 45592 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 92 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB218 | 45593 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 93 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB219 | 45594 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 94 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB21A | 45595 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 95 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB21B | 45596 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 96 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB21C | 45597 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 97 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB21D | 45598 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 98 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB21E | 45599 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 99 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital input | 0xB21F | 45600 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 2 of wireless device 100 • 0 = OFF // Inactive • 1 = ON // Active | [11 empty] | x
Digital output | 0xB220 | 45601 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 1 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB221 | 45602 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 2 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB222 | 45603 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 3 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB223 | 45604 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 4 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB224 | 45605 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 5 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB225 | 45606 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 6 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB226 | 45607 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 7 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB227 | 45608 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 8 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB228 | 45609 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 9 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB229 | 45610 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 10 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB22A | 45611 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 11 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB22B | 45612 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 12 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB22C | 45613 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 13 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB22D | 45614 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 14 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB22E | 45615 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 15 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB22F | 45616 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 16 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB230 | 45617 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 17 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB231 | 45618 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 18 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB232 | 45619 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 19 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB233 | 45620 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 20 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB234 | 45621 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 21 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB235 | 45622 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 22 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB236 | 45623 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 23 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB237 | 45624 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 24 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB238 | 45625 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 25 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB239 | 45626 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 26 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB23A | 45627 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 27 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB23B | 45628 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 28 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB23C | 45629 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 29 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB23D | 45630 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 30 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB23E | 45631 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 31 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB23F | 45632 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 32 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB240 | 45633 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 33 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB241 | 45634 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 34 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB242 | 45635 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 35 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB243 | 45636 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 36 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB244 | 45637 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 37 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB245 | 45638 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 38 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB246 | 45639 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 39 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB247 | 45640 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 40 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB248 | 45641 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 41 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB249 | 45642 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 42 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB24A | 45643 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 43 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB24B | 45644 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 44 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB24C | 45645 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 45 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB24D | 45646 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 46 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB24E | 45647 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 47 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB24F | 45648 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 48 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB250 | 45649 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 49 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB251 | 45650 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 50 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB252 | 45651 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 51 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB253 | 45652 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 52 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB254 | 45653 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 53 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB255 | 45654 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 54 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB256 | 45655 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 55 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB257 | 45656 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 56 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB258 | 45657 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 57 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB259 | 45658 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 58 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB25A | 45659 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 59 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB25B | 45660 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 60 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB25C | 45661 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 61 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB25D | 45662 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 62 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB25E | 45663 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 63 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB25F | 45664 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 64 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB260 | 45665 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 65 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB261 | 45666 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 66 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB262 | 45667 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 67 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB263 | 45668 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 68 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB264 | 45669 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 69 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB265 | 45670 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 70 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB266 | 45671 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 71 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB267 | 45672 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 72 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB268 | 45673 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 73 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB269 | 45674 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 74 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB26A | 45675 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 75 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB26B | 45676 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 76 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB26C | 45677 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 77 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB26D | 45678 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 78 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB26E | 45679 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 79 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB26F | 45680 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 80 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB270 | 45681 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 81 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB271 | 45682 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 82 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB272 | 45683 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 83 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB273 | 45684 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 84 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB274 | 45685 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 85 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB275 | 45686 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 86 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB276 | 45687 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 87 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB277 | 45688 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 88 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB278 | 45689 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 89 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB279 | 45690 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 90 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB27A | 45691 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 91 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB27B | 45692 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 92 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB27C | 45693 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 93 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB27D | 45694 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 94 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB27E | 45695 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 95 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB27F | 45696 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 96 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB280 | 45697 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 97 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB281 | 45698 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 98 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB282 | 45699 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 99 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB283 | 45700 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Sets the output status value of the wireless device 100 • 0 = No command • 1 = OffCommand // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) • 2 = OnCommand // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) • 3 =ToggleCommand // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay). Toggle can be used for Normal mode too } | [12 empty] | x
Digital output | 0xB284 | 45701 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 1 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB285 | 45702 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 2 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB286 | 45703 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 3 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB287 | 45704 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 4 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB288 | 45705 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 5 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB289 | 45706 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 6 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB28A | 45707 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 7 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB28B | 45708 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 8 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB28C | 45709 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 9 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB28D | 45710 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 10 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB28E | 45711 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 11 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB28F | 45712 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 12 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB290 | 45713 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 13 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB291 | 45714 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 14 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB292 | 45715 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 15 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB293 | 45716 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 16 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB294 | 45717 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 17 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB295 | 45718 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 18 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB296 | 45719 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 19 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB297 | 45720 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 20 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB298 | 45721 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 21 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB299 | 45722 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 22 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB29A | 45723 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 23 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB29B | 45724 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 24 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB29C | 45725 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 25 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB29D | 45726 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 26 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB29E | 45727 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 27 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB29F | 45728 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 28 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2A0 | 45729 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 29 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2A1 | 45730 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 30 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2A2 | 45731 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 31 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2A3 | 45732 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 32 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2A4 | 45733 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 33 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2A5 | 45734 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 34 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2A6 | 45735 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 35 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2A7 | 45736 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 36 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2A8 | 45737 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 37 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2A9 | 45738 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 38 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2AA | 45739 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 39 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2AB | 45740 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 40 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2AC | 45741 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 41 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2AD | 45742 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 42 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2AE | 45743 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 43 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2AF | 45744 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 44 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2B0 | 45745 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 45 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2B1 | 45746 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 46 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2B2 | 45747 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 47 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2B3 | 45748 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 48 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2B4 | 45749 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 49 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2B5 | 45750 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 50 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2B6 | 45751 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 51 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2B7 | 45752 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 52 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2B8 | 45753 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 53 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2B9 | 45754 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 54 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2BA | 45755 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 55 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2BB | 45756 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 56 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2BC | 45757 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 57 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2BD | 45758 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 58 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2BE | 45759 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 59 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2BF | 45760 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 60 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2C0 | 45761 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 61 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2C1 | 45762 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 62 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2C2 | 45763 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 63 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2C3 | 45764 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 64 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2C4 | 45765 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 65 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2C5 | 45766 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 66 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2C6 | 45767 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 67 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2C7 | 45768 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 68 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2C8 | 45769 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 69 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2C9 | 45770 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 70 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2CA | 45771 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 71 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2CB | 45772 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 72 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2CC | 45773 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 73 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2CD | 45774 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 74 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2CE | 45775 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 75 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2CF | 45776 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 76 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2D0 | 45777 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 77 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2D1 | 45778 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 78 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2D2 | 45779 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 79 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2D3 | 45780 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 80 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2D4 | 45781 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 81 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2D5 | 45782 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 82 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2D6 | 45783 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 83 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2D7 | 45784 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 84 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2D8 | 45785 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 85 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2D9 | 45786 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 86 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2DA | 45787 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 87 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2DB | 45788 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 88 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2DC | 45789 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 89 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2DD | 45790 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 90 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2DE | 45791 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 91 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2DF | 45792 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 92 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2E0 | 45793 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 93 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2E1 | 45794 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 94 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2E2 | 45795 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 95 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2E3 | 45796 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 96 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2E4 | 45797 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 97 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2E5 | 45798 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 98 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2E6 | 45799 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 99 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x
Digital output | 0xB2E7 | 45800 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output of the wireless device 100 • 0 = OFF // Inactive • 1 = ON // Active | [12 empty] | x

## PTE63-PoTag QO
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Current Metering Data | 0x0BB7 | 3000 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A
Current Metering Data | 0x0BB9 | 3002 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B
Current Metering Data | 0x0BBB | 3004 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C
Voltage Metering Data | 0x0BCB | 3020 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B
Voltage Metering Data | 0x0BCD | 3022 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C
Voltage Metering Data | 0x0BCF | 3024 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A
Voltage Metering Data | 0x0BD3 | 3028 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N
Voltage Metering Data | 0x0BD5 | 3030 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N
Voltage Metering Data | 0x0BD7 | 3032 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N
Power Metering Data | 0x0BED | 3054 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A
Power Metering Data | 0x0BEF | 3056 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B
Power Metering Data | 0x0BF1 | 3058 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C
Power Metering Data | 0x0BF3 | 3060 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power
Power Metering Data | 0x0C03 | 3076 | 2 | R | - | VA | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic)
Power Factor Metering Data | 0x0C0B | 3084 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor
Device Temperature Metering Data | 0x0C3B | 3132 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature
Energy Data - Legacy Zone | 0x0C83 | 3204 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Total active energy delivered + received (not resettable)
Energy Data - Legacy Zone | 0x0C87 | 3208 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Total active energy delivered count positively (not resettable)
Energy Data - Legacy Zone | 0x0C8B | 3212 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Total active energy received (not resettable)
Energy Data - Legacy Zone | 0x0CB7 | 3256 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial active energy delivered + received (resettable)
Energy Data - Legacy Zone | 0x0CBB | 3260 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial active energy counter. The value returns to zero by Panel Server.
Energy Data - Legacy Zone | 0x0CBF | 3264 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial active energy delivered (resettable)
Energy Data - Legacy Zone | 0x0CC3 | 3268 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial active energy delivered counter. The value returns to zero by Panel Server.
Energy Data - Legacy Zone | 0x0CC7 | 3272 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial active energy received (resettable)
Energy Data - Legacy Zone | 0x0CCB | 3276 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial active energy received counter. The value returns to zero by Panel Server.
Load Monitoring - Alarm | 0x0CE1 | 3298 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) – refer to register 3300 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active
Load Monitoring - Alarm | 0x0CE3 | 3300 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active
Load Monitoring - Alarm | 0x0CE5 | 3302 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Last RMS current measured on phase B when voltage loss occurred
Load Monitoring - Alarm | 0x0CE7 | 3304 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Last RMS current measured on phase A when voltage loss occurred
Load Monitoring - Alarm | 0x0CE9 | 3306 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Last RMS current measured on phase C when voltage loss occurred
Load Monitoring - Alarm | 0x0CED | 3310 | 2 | R | - | W | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Active power threshold for load operating time counter. Counter starts above the threshold value.
Power Demand Data | 0x0EB5 | 3766 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power
Power Demand Data | 0x0EB9 | 3770 | 2 | R | - | W | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Peak demand total active power
Power Demand Data | 0x0EBB | 3772 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Peak demand total active power timestamp
Energy Data – New Zone | 0x1390 | 5009 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy delivered (resettable)
Energy Data – New Zone | 0x1394 | 5013 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy delivered count positively (not resettable)
Energy Data – New Zone | 0x1398 | 5017 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy received (resettable)
Energy Data – New Zone | 0x139C | 5021 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy received count negatively (not resettable)
Energy Data – New Zone | 0x13B8 | 5049 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase A delivered (resettable)
Energy Data – New Zone | 0x13BC | 5053 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase A delivered (not resettable)
Energy Data – New Zone | 0x13C0 | 5057 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase A received (resettable)
Energy Data – New Zone | 0x13C4 | 5061 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase A received (not resettable)
Energy Data – New Zone | 0x13E0 | 5089 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase B delivered (resettable)
Energy Data – New Zone | 0x13E4 | 5093 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase B delivered (not resettable)
Energy Data – New Zone | 0x13E8 | 5097 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase B received (resettable)
Energy Data – New Zone | 0x13EC | 5101 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase B received (not resettable)
Energy Data – New Zone | 0x1408 | 5129 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase C delivered (resettable)
Energy Data – New Zone | 0x140C | 5133 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase C delivered (not resettable)
Energy Data – New Zone | 0x1410 | 5137 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase C received (resettable)
Energy Data – New Zone | 0x1414 | 5141 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase C received (not resettable)
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Configuration | 0x7925 | 31014 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the usage of the wireless device with: • 1 = Main/Incomer • 2 = Sub/Head of group • 3 = Heating • 4 = Cooling • 5 = HVAC • 6 = Ventilation • 7 = Lighting • 8 = Office Equipment • 9 = Cooking • 10 = Food refrigeration • 11 = Elevators • 12 = Computers • 13 = Renewable power source • 14 = Genset • 15 = Compressed air • 16 = Vapor • 17 = Machine • 18 = Process • 19 = Water • 20 = Other Sockets • 21 = Other • 22 = Electrical vehicle charging station • 23 = Loads associated with renewable power source • 24 = Plug loads • 25 = Air conditionning • 26 = Domestic hot water • 27 = Heating & air conditionning • 28 = Hot sanitary water • 29 = IT • 30 = Lighting (interior) • 31 = Lighting (exterior and park) • 32 = Mixed usages • 33 = Refrigeration • 34 = Special loads • 35 = Total • 36 = Transportation system • 37 = Water system pumps • 38 = Emergency lighting
Configuration | 0x7926 | 31015 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Phase sequence with: • 1 = Phase A • 2 = Phase B • 3 = Phase C • 4 = Phase sequence ABC or AB • 5 = Phase sequence ACB or AC • 6 = Phase sequence BCA or BC • 7 = Phase sequence BAC or BA • 8 = Phase sequence CAB or CA • 9 = Phase sequence CBA or CB
Configuration | 0x7927 | 31016 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Mounting position • 0 = Not configured • 1 = Top • 2 = Bottom • 3 = Not applicable
Configuration | 0x7929 | 31018 | 1 | R | - | A | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Rated current of the protective device to the wireless device
Configuration | 0x792B | 31020 | 2 | R | - | V | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Rated voltage: • LN rated voltage for single phase wiring systems • LL rated voltage for 3 phases wiring systems
Configuration | 0x792D | 31022 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the commodity of the wireless device 1. Electricity 2. Gas 3. Fuel oil 4. Air 5. Steam 6. Water 7. Environment 8. Other 9. Custom (Free text to enter): User can enter 10 custom values
Configuration | 0x792E | 31023 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Reset the Peak Active Power Demand for this wireless device, Any value writen will reset Peak Active Power Demand to 0
Configuration | 0x792F | 31024 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Power supply type • 1 = Top • 2 = Bottom (default value)
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier : 16131 - LV933071W, LV933072W, LV933073W 16132 - LV947600W, LV947602W, LV947603W 17200 - A9MEM1520 17201 - A9MEM1521 17202 - A9MEM1522 17203 - A9MEM1540 17204 - A9MEM1541 17205 - A9MEM1542 17206 - A9MEM1560 17207 - A9MEM1561 17208 - A9MEM1562 17209 - A9MEM1563 17210 - A9MEM1570 17211 - A9MEM1571 17212 - A9MEM1572 17213 - A9MEM1543 17214 - A9MEM1573 17215 - A9MEM1564 17216 - A9MEM1574 17218 - A9MEM1575 17300 - EMS59440 17301 - EMS59443 17302 - A9XST114, ESST010B0400 17305 - SED-CO2-G-5045 17306 - SED-TRH-G-5045 17308 - PD100X001 17320 - SPTH150S 17321 - SPTH150M 17322 - SPTH200M 17350 - SMT10020 (V1) 17351 - SMT10020 (V2) 17660 - OVA44210, OVA44211, OVA44212, OVA44213, OVA44214, OVA44215, OVA47210, OVA47211, OVA47212, OVA47213, OVA47214, OVA47215, OVA59130, OVA59131, OVA59132, OVA59230, OVA59231, OVA59330, OVA59331, OV59430, OVA59431 17750 - LV429453 17751 - LV429454 17800 - LV434020 17801 - LV434021 17802 - LV434022 17803 - LV434023 17854 - PLTPPB1253P 17900 - A9XMC2D3 17901 - A9XMC1D3 17950 - PLTQO301P 17951 - PLTQO601P 17952 - PLTQO302P 17953 - PLTQO602P 17954 - PLTQO303P 17955 - PLTQO603P 17956 - PLTE601P 17957 - PLTE602P 17958 - PLTE603P 17969 - PLTR1203P 17970 - PLTR6003P 17971 - PLTR10003P 17972 - PLTR20003P 17973 - A9MEM1590 17974 - A9MEM1591 17975 - A9MEM1592 17976 - A9MEM1593 17980 - A9MEM1580 19500 - A9TYBE625, A9TYBE640 19501 - A9TAB1625, A9TAB1640, A9TAB2625, A9TAB2640 19502 - A9TDEC610, A9TDEC613, A9TDEC616, A9TDFC606, A9TDFC610, A9TDFC613, A9TDFC616, A9TDFC625, A9TDFC632, A9TDFC640, A9TDFD606, A9TDFD610, A9TDFD616, A9TDFD620, A9TDFD625, A9TDFD632 19503 - A9TPDD610, A9TPDD613, A9TPDD616, A9TPED610, A9TPED613, A9TPED616, A9TPED625, A9TPED632, A9TPED640 19504 - A9TYAE225, A9TYAE240, A9TYBE225, A9TYBE240 19505 - A9TAA1225, A9TAA1240, A9TAA225, A9TAA2240, A9TAB1225, A9TAB1240, A9TAB2225, A9TAB2240 19506 - A9TYAE625, A9TYAE640 19507 - A9TAA1625, A9TAA1640, A9TAA2625, A9TAA2640 19508 - A9TDND606, A9TDND610, A9TDND616, A9TDND620, A9TDND625, A9TDND632, A9TDNC606, A9TDNC610, A9TDNC616, A9TDNC625, A9TDNC632, A9TDNC640 19600 - A9V6E225, A9V6E240, A9V8E225, A9V8E240, A9Y6E625, A9Y6E640, A9Y8E625, A9Y8E640 20200 - ZBRT1 20201 - ZBRT2
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the device and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79AA | 31147 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Packet Error Rate (PER) of the device, received by Panel Server
Diagnostic Data | 0x79AC | 31149 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI of the device, received by Panel Server
Diagnostic Data | 0x79AE | 31151 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Link Quality Indicator (LQI) of the device, received by Panel Server
Diagnostic Data | 0x79AF | 31152 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER of gateway, calculated inside the Panel Server
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B4 | 31157 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER – Maximum value between device and Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server

## PTEnergy250_630-PoTag Efram
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Current Metering Data | 0x0BB7 | 3000 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A
Current Metering Data | 0x0BB9 | 3002 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B
Current Metering Data | 0x0BBB | 3004 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C
Voltage Metering Data | 0x0BCB | 3020 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B
Voltage Metering Data | 0x0BCD | 3022 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C
Voltage Metering Data | 0x0BCF | 3024 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A
Voltage Metering Data | 0x0BD3 | 3028 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N
Voltage Metering Data | 0x0BD5 | 3030 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N
Voltage Metering Data | 0x0BD7 | 3032 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N
Power Metering Data | 0x0BED | 3054 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A
Power Metering Data | 0x0BEF | 3056 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B
Power Metering Data | 0x0BF1 | 3058 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C
Power Metering Data | 0x0BF3 | 3060 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power
Power Metering Data | 0x0BFB | 3068 | 2 | R | - | VAR | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power
Power Metering Data | 0x0C03 | 3076 | 2 | R | - | VA | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic)
Power Factor Metering Data | 0x0C0B | 3084 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor
Power Factor Metering Data | 0x0C0D | 3086 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Power factor sign convention • 0 = IEC • 1 = IEEE
Frequency Metering Data | 0x0C25 | 3110 | 2 | R | - | Hz | Float32 |  | 0xFFC00000 | N | 3, 100-4 | AC frequency
Device Temperature Metering Data | 0x0C3B | 3132 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature
Energy Data - Legacy Zone | 0x0C83 | 3204 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Total active energy delivered + received (not resettable)
Energy Data - Legacy Zone | 0x0C87 | 3208 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Total active energy delivered count positively (not resettable)
Energy Data - Legacy Zone | 0x0C8B | 3212 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Total active energy received (not resettable)
Energy Data - Legacy Zone | 0x0C8F | 3216 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase A delivered – received (not resettable)
Energy Data - Legacy Zone | 0x0C93 | 3220 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase B delivered – received (not resettable)
Energy Data - Legacy Zone | 0x0C97 | 3224 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase C delivered – received (not resettable)
Energy Data - Legacy Zone | 0x0CB7 | 3256 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial active energy delivered + received (resettable)
Energy Data - Legacy Zone | 0x0CBB | 3260 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial active energy counter. The value returns to zero by Panel Server.
Energy Data - Legacy Zone | 0x0CBF | 3264 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial active energy delivered (resettable)
Energy Data - Legacy Zone | 0x0CC3 | 3268 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial active energy delivered counter. The value returns to zero by Panel Server.
Energy Data - Legacy Zone | 0x0CC7 | 3272 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial active energy received (resettable)
Energy Data - Legacy Zone | 0x0CCB | 3276 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial active energy received counter. The value returns to zero by Panel Server.
Energy Data - Legacy Zone | 0x0CCF | 3280 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial reactive energy delivered (resettable)
Energy Data - Legacy Zone | 0x0CD3 | 3284 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial reactive energy delivered counter. The value returns to zero by Panel Server.
Energy Data - Legacy Zone | 0x0CD7 | 3288 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial reactive energy received (resettable)
Energy Data - Legacy Zone | 0x0CDB | 3292 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial reactive energy received counter. The value returns to zero by Panel Server.
Load Monitoring - Alarm | 0x0CE1 | 3298 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) – refer to register 3300 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active
Load Monitoring - Alarm | 0x0CE3 | 3300 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active
Load Monitoring - Alarm | 0x0CE5 | 3302 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Last RMS current measured on phase B when voltage loss occurred
Load Monitoring - Alarm | 0x0CE7 | 3304 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Last RMS current measured on phase A when voltage loss occurred
Load Monitoring - Alarm | 0x0CE9 | 3306 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Last RMS current measured on phase C when voltage loss occurred
Load Monitoring - Alarm | 0x0CED | 3310 | 2 | R | - | W | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Active power threshold for load operating time counter. Counter starts above the threshold value.
Power Demand Data | 0x0EB5 | 3766 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power
Power Demand Data | 0x0EB9 | 3770 | 2 | R | - | W | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Peak demand total active power
Power Demand Data | 0x0EBB | 3772 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Peak demand total active power timestamp
Energy Data – New Zone | 0x1390 | 5009 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy delivered (resettable)
Energy Data – New Zone | 0x1398 | 5017 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy received (resettable)
Energy Data – New Zone | 0x1438 | 5177 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy delivered (resettable)
Energy Data – New Zone | 0x1448 | 5193 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy received (resettable)
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Configuration | 0x7925 | 31014 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the usage of the wireless device with: • 1 = Main/Incomer • 2 = Sub/Head of group • 3 = Heating • 4 = Cooling • 5 = HVAC • 6 = Ventilation • 7 = Lighting • 8 = Office Equipment • 9 = Cooking • 10 = Food refrigeration • 11 = Elevators • 12 = Computers • 13 = Renewable power source • 14 = Genset • 15 = Compressed air • 16 = Vapor • 17 = Machine • 18 = Process • 19 = Water • 20 = Other Sockets • 21 = Other • 22 = Electrical vehicle charging station • 23 = Loads associated with renewable power source • 24 = Plug loads • 25 = Air conditionning • 26 = Domestic hot water • 27 = Heating & air conditionning • 28 = Hot sanitary water • 29 = IT • 30 = Lighting (interior) • 31 = Lighting (exterior and park) • 32 = Mixed usages • 33 = Refrigeration • 34 = Special loads • 35 = Total • 36 = Transportation system • 37 = Water system pumps • 38 = Emergency lighting
Configuration | 0x7926 | 31015 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Phase sequence with: • 1 = Phase A • 2 = Phase B • 3 = Phase C • 4 = Phase sequence ABC or AB • 5 = Phase sequence ACB or AC • 6 = Phase sequence BCA or BC • 7 = Phase sequence BAC or BA • 8 = Phase sequence CAB or CA • 9 = Phase sequence CBA or CB
Configuration | 0x7927 | 31016 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Mounting position • 0 = Not configured • 1 = Top • 2 = Bottom • 3 = Not applicable
Configuration | 0x7929 | 31018 | 1 | R | - | A | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Rated current of the protective device to the wireless device
Configuration | 0x792A | 31019 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Electrical network system type • 0 = Unknown system type • 3 = 3PH3W • 11= 3PH4W
Configuration | 0x792B | 31020 | 2 | R | - | V | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Rated voltage: • LN rated voltage for single phase wiring systems • LL rated voltage for 3 phases wiring systems
Configuration | 0x792D | 31022 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the commodity of the wireless device 1. Electricity 2. Gas 3. Fuel oil 4. Air 5. Steam 6. Water 7. Environment 8. Other 9. Custom (Free text to enter): User can enter 10 custom values
Configuration | 0x792E | 31023 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Reset the Peak Active Power Demand for this wireless device, Any value writen will reset Peak Active Power Demand to 0
Configuration | 0x792F | 31024 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Power supply type • 1 = Top • 2 = Bottom (default value)
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier : 16131 - LV933071W, LV933072W, LV933073W 16132 - LV947600W, LV947602W, LV947603W 17200 - A9MEM1520 17201 - A9MEM1521 17202 - A9MEM1522 17203 - A9MEM1540 17204 - A9MEM1541 17205 - A9MEM1542 17206 - A9MEM1560 17207 - A9MEM1561 17208 - A9MEM1562 17209 - A9MEM1563 17210 - A9MEM1570 17211 - A9MEM1571 17212 - A9MEM1572 17213 - A9MEM1543 17214 - A9MEM1573 17215 - A9MEM1564 17216 - A9MEM1574 17218 - A9MEM1575 17300 - EMS59440 17301 - EMS59443 17302 - A9XST114, ESST010B0400 17305 - SED-CO2-G-5045 17306 - SED-TRH-G-5045 17308 - PD100X001 17320 - SPTH150S 17321 - SPTH150M 17322 - SPTH200M 17350 - SMT10020 (V1) 17351 - SMT10020 (V2) 17660 - OVA44210, OVA44211, OVA44212, OVA44213, OVA44214, OVA44215, OVA47210, OVA47211, OVA47212, OVA47213, OVA47214, OVA47215, OVA59130, OVA59131, OVA59132, OVA59230, OVA59231, OVA59330, OVA59331, OV59430, OVA59431 17750 - LV429453 17751 - LV429454 17800 - LV434020 17801 - LV434021 17802 - LV434022 17803 - LV434023 17854 - PLTPPB1253P 17900 - A9XMC2D3 17901 - A9XMC1D3 17950 - PLTQO301P 17951 - PLTQO601P 17952 - PLTQO302P 17953 - PLTQO602P 17954 - PLTQO303P 17955 - PLTQO603P 17956 - PLTE601P 17957 - PLTE602P 17958 - PLTE603P 17969 - PLTR1203P 17970 - PLTR6003P 17971 - PLTR10003P 17972 - PLTR20003P 17973 - A9MEM1590 17974 - A9MEM1591 17975 - A9MEM1592 17976 - A9MEM1593 17980 - A9MEM1580 19500 - A9TYBE625, A9TYBE640 19501 - A9TAB1625, A9TAB1640, A9TAB2625, A9TAB2640 19502 - A9TDEC610, A9TDEC613, A9TDEC616, A9TDFC606, A9TDFC610, A9TDFC613, A9TDFC616, A9TDFC625, A9TDFC632, A9TDFC640, A9TDFD606, A9TDFD610, A9TDFD616, A9TDFD620, A9TDFD625, A9TDFD632 19503 - A9TPDD610, A9TPDD613, A9TPDD616, A9TPED610, A9TPED613, A9TPED616, A9TPED625, A9TPED632, A9TPED640 19504 - A9TYAE225, A9TYAE240, A9TYBE225, A9TYBE240 19505 - A9TAA1225, A9TAA1240, A9TAA225, A9TAA2240, A9TAB1225, A9TAB1240, A9TAB2225, A9TAB2240 19506 - A9TYAE625, A9TYAE640 19507 - A9TAA1625, A9TAA1640, A9TAA2625, A9TAA2640 19508 - A9TDND606, A9TDND610, A9TDND616, A9TDND620, A9TDND625, A9TDND632, A9TDNC606, A9TDNC610, A9TDNC616, A9TDNC625, A9TDNC632, A9TDNC640 19600 - A9V6E225, A9V6E240, A9V8E225, A9V8E240, A9Y6E625, A9Y6E640, A9Y8E625, A9Y8E640 20200 - ZBRT1 20201 - ZBRT2
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the device and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79AA | 31147 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Packet Error Rate (PER) of the device, received by Panel Server
Diagnostic Data | 0x79AC | 31149 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI of the device, received by Panel Server
Diagnostic Data | 0x79AE | 31151 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Link Quality Indicator (LQI) of the device, received by Panel Server
Diagnostic Data | 0x79AF | 31152 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER of gateway, calculated inside the Panel Server
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B4 | 31157 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER – Maximum value between device and Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server

## PTE Rope-PoTag Rope
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Current Metering Data | 0x0BB7 | 3000 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A
Current Metering Data | 0x0BB9 | 3002 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B
Current Metering Data | 0x0BBB | 3004 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C
Current Metering Data | 0x0BBD | 3006 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral
Voltage Metering Data | 0x0BCB | 3020 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B
Voltage Metering Data | 0x0BCD | 3022 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C
Voltage Metering Data | 0x0BCF | 3024 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A
Voltage Metering Data | 0x0BD3 | 3028 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N
Voltage Metering Data | 0x0BD5 | 3030 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N
Voltage Metering Data | 0x0BD7 | 3032 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N
Power Metering Data | 0x0BED | 3054 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A
Power Metering Data | 0x0BEF | 3056 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B
Power Metering Data | 0x0BF1 | 3058 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C
Power Metering Data | 0x0BF3 | 3060 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power
Power Metering Data | 0x0BF5 | 3062 | 2 | R | - | VAR | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Reactive power on phase A
Power Metering Data | 0x0BF7 | 3064 | 2 | R | - | VAR | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Reactive power on phase B
Power Metering Data | 0x0BF9 | 3066 | 2 | R | - | VAR | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Reactive power on phase C
Power Metering Data | 0x0BFB | 3068 | 2 | R | - | VAR | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power
Power Metering Data | 0x0BFD | 3070 | 2 | R | - | VA | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Apparent power on phase A
Power Metering Data | 0x0BFF | 3072 | 2 | R | - | VA | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Apparent power on phase B
Power Metering Data | 0x0C01 | 3074 | 2 | R | - | VA | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Apparent power on phase C
Power Metering Data | 0x0C03 | 3076 | 2 | R | - | VA | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic)
Power Factor Metering Data | 0x0C05 | 3078 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Power factor on phase A
Power Factor Metering Data | 0x0C07 | 3080 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Power factor on phase B
Power Factor Metering Data | 0x0C09 | 3082 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Power factor on phase C
Power Factor Metering Data | 0x0C0B | 3084 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor
Power Factor Metering Data | 0x0C0D | 3086 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Power factor sign convention • 0 = IEC • 1 = IEEE
Frequency Metering Data | 0x0C25 | 3110 | 2 | R | - | Hz | Float32 |  | 0xFFC00000 | N | 3, 100-4 | AC frequency
Device Temperature Metering Data | 0x0C3B | 3132 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature
Energy Data - Legacy Zone | 0x0C83 | 3204 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Total active energy delivered + received (not resettable)
Energy Data - Legacy Zone | 0x0C87 | 3208 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Total active energy delivered count positively (not resettable)
Energy Data - Legacy Zone | 0x0C8B | 3212 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Total active energy received (not resettable)
Energy Data - Legacy Zone | 0x0CB7 | 3256 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial active energy delivered + received (resettable)
Energy Data - Legacy Zone | 0x0CBB | 3260 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial active energy counter. The value returns to zero by Panel Server.
Energy Data - Legacy Zone | 0x0CBF | 3264 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial active energy delivered (resettable)
Energy Data - Legacy Zone | 0x0CC3 | 3268 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial active energy delivered counter. The value returns to zero by Panel Server.
Energy Data - Legacy Zone | 0x0CC7 | 3272 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial active energy received (resettable)
Energy Data - Legacy Zone | 0x0CCB | 3276 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial active energy received counter. The value returns to zero by Panel Server.
Energy Data - Legacy Zone | 0x0CCF | 3280 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial reactive energy delivered (resettable)
Energy Data - Legacy Zone | 0x0CD3 | 3284 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial reactive energy delivered counter. The value returns to zero by Panel Server.
Energy Data - Legacy Zone | 0x0CD7 | 3288 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial reactive energy received (resettable)
Energy Data - Legacy Zone | 0x0CDB | 3292 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial reactive energy received counter. The value returns to zero by Panel Server.
Load Monitoring - Alarm | 0x0CE1 | 3298 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) – refer to register 3300 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active
Load Monitoring - Alarm | 0x0CE3 | 3300 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active
Load Monitoring - Alarm | 0x0CE5 | 3302 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Last RMS current measured on phase B when voltage loss occurred
Load Monitoring - Alarm | 0x0CE7 | 3304 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Last RMS current measured on phase A when voltage loss occurred
Load Monitoring - Alarm | 0x0CE9 | 3306 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Last RMS current measured on phase C when voltage loss occurred
Load Monitoring - Alarm | 0x0CED | 3310 | 2 | R | - | W | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Active power threshold for load operating time counter. Counter starts above the threshold value.
Power Demand Data | 0x0EB5 | 3766 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power
Power Demand Data | 0x0EB9 | 3770 | 2 | R | - | W | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Peak demand total active power
Power Demand Data | 0x0EBB | 3772 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Peak demand total active power timestamp
Energy Data – New Zone | 0x1390 | 5009 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy delivered (resettable)
Energy Data – New Zone | 0x1394 | 5013 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy delivered count positively (not resettable)
Energy Data – New Zone | 0x1398 | 5017 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy received (resettable)
Energy Data – New Zone | 0x139C | 5021 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy received count negatively (not resettable)
Energy Data – New Zone | 0x13B8 | 5049 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase A delivered (resettable)
Energy Data – New Zone | 0x13BC | 5053 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase A delivered (not resettable)
Energy Data – New Zone | 0x13C0 | 5057 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase A received (resettable)
Energy Data – New Zone | 0x13C4 | 5061 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase A received (not resettable)
Energy Data – New Zone | 0x13E0 | 5089 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase B delivered (resettable)
Energy Data – New Zone | 0x13E4 | 5093 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase B delivered (not resettable)
Energy Data – New Zone | 0x13E8 | 5097 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase B received (resettable)
Energy Data – New Zone | 0x13EC | 5101 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase B received (not resettable)
Energy Data – New Zone | 0x1408 | 5129 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase C delivered (resettable)
Energy Data – New Zone | 0x140C | 5133 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase C delivered (not resettable)
Energy Data – New Zone | 0x1410 | 5137 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase C received (resettable)
Energy Data – New Zone | 0x1414 | 5141 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase C received (not resettable)
Energy Data – New Zone | 0x1438 | 5177 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy delivered (resettable)
Energy Data – New Zone | 0x143C | 5181 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy delivered count positively (not resettable)
Energy Data – New Zone | 0x1448 | 5193 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy received (resettable)
Energy Data – New Zone | 0x144C | 5197 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy received count negatively (not resettable)
Energy Data – New Zone | 0x1470 | 5233 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy on phase A delivered (resettable)
Energy Data – New Zone | 0x1474 | 5237 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy on phase A delivered (not resettable)
Energy Data – New Zone | 0x1478 | 5241 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy on phase A received (resettable)
Energy Data – New Zone | 0x147C | 5245 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy on phase A received (not resettable)
Energy Data – New Zone | 0x1498 | 5273 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy on phase B delivered (resettable)
Energy Data – New Zone | 0x149C | 5277 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy on phase B delivered (not resettable)
Energy Data – New Zone | 0x14A0 | 5281 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy on phase B received (resettable)
Energy Data – New Zone | 0x14A4 | 5285 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy on phase B received (not resettable)
Energy Data – New Zone | 0x14C0 | 5313 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy on phase C delivered (resettable)
Energy Data – New Zone | 0x14C4 | 5317 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy on phase C delivered (not resettable)
Energy Data – New Zone | 0x14C8 | 5321 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy on phase C received (resettable)
Energy Data – New Zone | 0x14CC | 5325 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy on phase C received (not resettable)
Energy Data – New Zone | 0x14F4 | 5365 | 4 | RW | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Apparent energy delivered + received (resettable)
Energy Data – New Zone | 0x14F8 | 5369 | 4 | R | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Apparent energy delivered + received (not resettable)
Energy Data – New Zone | 0x150C | 5389 | 4 | RW | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Apparent energy on phase A (resettable)
Energy Data – New Zone | 0x1510 | 5393 | 4 | R | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Apparent energy on phase A (not resettable)
Energy Data – New Zone | 0x1534 | 5429 | 4 | RW | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Apparent energy on phase B (resettable)
Energy Data – New Zone | 0x1538 | 5433 | 4 | R | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Apparent energy on phase B (not resettable)
Energy Data – New Zone | 0x155C | 5469 | 4 | RW | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Apparent energy on phase C (resettable)
Energy Data – New Zone | 0x1560 | 5473 | 4 | R | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Apparent energy on phase C (not resettable)
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Configuration | 0x7925 | 31014 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the usage of the wireless device with: • 1 = Main/Incomer • 2 = Sub/Head of group • 3 = Heating • 4 = Cooling • 5 = HVAC • 6 = Ventilation • 7 = Lighting • 8 = Office Equipment • 9 = Cooking • 10 = Food refrigeration • 11 = Elevators • 12 = Computers • 13 = Renewable power source • 14 = Genset • 15 = Compressed air • 16 = Vapor • 17 = Machine • 18 = Process • 19 = Water • 20 = Other Sockets • 21 = Other • 22 = Electrical vehicle charging station • 23 = Loads associated with renewable power source • 24 = Plug loads • 25 = Air conditionning • 26 = Domestic hot water • 27 = Heating & air conditionning • 28 = Hot sanitary water • 29 = IT • 30 = Lighting (interior) • 31 = Lighting (exterior and park) • 32 = Mixed usages • 33 = Refrigeration • 34 = Special loads • 35 = Total • 36 = Transportation system • 37 = Water system pumps • 38 = Emergency lighting
Configuration | 0x7926 | 31015 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Phase sequence with: • 1 = Phase A • 2 = Phase B • 3 = Phase C • 4 = Phase sequence ABC or AB • 5 = Phase sequence ACB or AC • 6 = Phase sequence BCA or BC • 7 = Phase sequence BAC or BA • 8 = Phase sequence CAB or CA • 9 = Phase sequence CBA or CB
Configuration | 0x7927 | 31016 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Mounting position • 0 = Not configured • 1 = Top • 2 = Bottom • 3 = Not applicable
Configuration | 0x7929 | 31018 | 1 | R | - | A | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Rated current of the protective device to the wireless device
Configuration | 0x792A | 31019 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Electrical network system type • 0 = Unknown system type • 3 = 3PH3W • 11= 3PH4W
Configuration | 0x792B | 31020 | 2 | R | - | V | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Rated voltage: • LN rated voltage for single phase wiring systems • LL rated voltage for 3 phases wiring systems
Configuration | 0x792D | 31022 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the commodity of the wireless device 1. Electricity 2. Gas 3. Fuel oil 4. Air 5. Steam 6. Water 7. Environment 8. Other 9. Custom (Free text to enter): User can enter 10 custom values
Configuration | 0x792E | 31023 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Reset the Peak Active Power Demand for this wireless device, Any value writen will reset Peak Active Power Demand to 0
Configuration | 0x792F | 31024 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Power supply type • 1 = Top • 2 = Bottom (default value)
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier : 16131 - LV933071W, LV933072W, LV933073W 16132 - LV947600W, LV947602W, LV947603W 17200 - A9MEM1520 17201 - A9MEM1521 17202 - A9MEM1522 17203 - A9MEM1540 17204 - A9MEM1541 17205 - A9MEM1542 17206 - A9MEM1560 17207 - A9MEM1561 17208 - A9MEM1562 17209 - A9MEM1563 17210 - A9MEM1570 17211 - A9MEM1571 17212 - A9MEM1572 17213 - A9MEM1543 17214 - A9MEM1573 17215 - A9MEM1564 17216 - A9MEM1574 17218 - A9MEM1575 17300 - EMS59440 17301 - EMS59443 17302 - A9XST114, ESST010B0400 17305 - SED-CO2-G-5045 17306 - SED-TRH-G-5045 17308 - PD100X001 17320 - SPTH150S 17321 - SPTH150M 17322 - SPTH200M 17350 - SMT10020 (V1) 17351 - SMT10020 (V2) 17660 - OVA44210, OVA44211, OVA44212, OVA44213, OVA44214, OVA44215, OVA47210, OVA47211, OVA47212, OVA47213, OVA47214, OVA47215, OVA59130, OVA59131, OVA59132, OVA59230, OVA59231, OVA59330, OVA59331, OV59430, OVA59431 17750 - LV429453 17751 - LV429454 17800 - LV434020 17801 - LV434021 17802 - LV434022 17803 - LV434023 17854 - PLTPPB1253P 17900 - A9XMC2D3 17901 - A9XMC1D3 17950 - PLTQO301P 17951 - PLTQO601P 17952 - PLTQO302P 17953 - PLTQO602P 17954 - PLTQO303P 17955 - PLTQO603P 17956 - PLTE601P 17957 - PLTE602P 17958 - PLTE603P 17969 - PLTR1203P 17970 - PLTR6003P 17971 - PLTR10003P 17972 - PLTR20003P 17973 - A9MEM1590 17974 - A9MEM1591 17975 - A9MEM1592 17976 - A9MEM1593 17980 - A9MEM1580 19500 - A9TYBE625, A9TYBE640 19501 - A9TAB1625, A9TAB1640, A9TAB2625, A9TAB2640 19502 - A9TDEC610, A9TDEC613, A9TDEC616, A9TDFC606, A9TDFC610, A9TDFC613, A9TDFC616, A9TDFC625, A9TDFC632, A9TDFC640, A9TDFD606, A9TDFD610, A9TDFD616, A9TDFD620, A9TDFD625, A9TDFD632 19503 - A9TPDD610, A9TPDD613, A9TPDD616, A9TPED610, A9TPED613, A9TPED616, A9TPED625, A9TPED632, A9TPED640 19504 - A9TYAE225, A9TYAE240, A9TYBE225, A9TYBE240 19505 - A9TAA1225, A9TAA1240, A9TAA225, A9TAA2240, A9TAB1225, A9TAB1240, A9TAB2225, A9TAB2240 19506 - A9TYAE625, A9TYAE640 19507 - A9TAA1625, A9TAA1640, A9TAA2625, A9TAA2640 19508 - A9TDND606, A9TDND610, A9TDND616, A9TDND620, A9TDND625, A9TDND632, A9TDNC606, A9TDNC610, A9TDNC616, A9TDNC625, A9TDNC632, A9TDNC640 19600 - A9V6E225, A9V6E240, A9V8E225, A9V8E240, A9Y6E625, A9Y6E640, A9Y8E625, A9Y8E640 20200 - ZBRT1 20201 - ZBRT2
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the device and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79AA | 31147 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Packet Error Rate (PER) of the device, received by Panel Server
Diagnostic Data | 0x79AC | 31149 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI of the device, received by Panel Server
Diagnostic Data | 0x79AE | 31151 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Link Quality Indicator (LQI) of the device, received by Panel Server
Diagnostic Data | 0x79AF | 31152 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER of gateway, calculated inside the Panel Server
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B4 | 31157 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER – Maximum value between device and Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server

## TH110
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Device Temperature Metering Data | 0x0C3B | 3132 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature
Ambient Data | 0x0FA0 | 4001 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value
Ambient Data | 0x0FA2 | 4003 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Maximum value that the device is able to read (maximum measurable temperature).
Ambient Data | 0x0FA4 | 4005 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Minimum value that the device is able to read (minimum measurable temperature).
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Configuration | 0x792D | 31022 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the commodity of the wireless device 1. Electricity 2. Gas 3. Fuel oil 4. Air 5. Steam 6. Water 7. Environment 8. Other 9. Custom (Free text to enter): User can enter 10 custom values
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier : 16131 - LV933071W, LV933072W, LV933073W 16132 - LV947600W, LV947602W, LV947603W 17200 - A9MEM1520 17201 - A9MEM1521 17202 - A9MEM1522 17203 - A9MEM1540 17204 - A9MEM1541 17205 - A9MEM1542 17206 - A9MEM1560 17207 - A9MEM1561 17208 - A9MEM1562 17209 - A9MEM1563 17210 - A9MEM1570 17211 - A9MEM1571 17212 - A9MEM1572 17213 - A9MEM1543 17214 - A9MEM1573 17215 - A9MEM1564 17216 - A9MEM1574 17218 - A9MEM1575 17300 - EMS59440 17301 - EMS59443 17302 - A9XST114, ESST010B0400 17305 - SED-CO2-G-5045 17306 - SED-TRH-G-5045 17308 - PD100X001 17320 - SPTH150S 17321 - SPTH150M 17322 - SPTH200M 17350 - SMT10020 (V1) 17351 - SMT10020 (V2) 17660 - OVA44210, OVA44211, OVA44212, OVA44213, OVA44214, OVA44215, OVA47210, OVA47211, OVA47212, OVA47213, OVA47214, OVA47215, OVA59130, OVA59131, OVA59132, OVA59230, OVA59231, OVA59330, OVA59331, OV59430, OVA59431 17750 - LV429453 17751 - LV429454 17800 - LV434020 17801 - LV434021 17802 - LV434022 17803 - LV434023 17854 - PLTPPB1253P 17900 - A9XMC2D3 17901 - A9XMC1D3 17950 - PLTQO301P 17951 - PLTQO601P 17952 - PLTQO302P 17953 - PLTQO602P 17954 - PLTQO303P 17955 - PLTQO603P 17956 - PLTE601P 17957 - PLTE602P 17958 - PLTE603P 17969 - PLTR1203P 17970 - PLTR6003P 17971 - PLTR10003P 17972 - PLTR20003P 17973 - A9MEM1590 17974 - A9MEM1591 17975 - A9MEM1592 17976 - A9MEM1593 17980 - A9MEM1580 19500 - A9TYBE625, A9TYBE640 19501 - A9TAB1625, A9TAB1640, A9TAB2625, A9TAB2640 19502 - A9TDEC610, A9TDEC613, A9TDEC616, A9TDFC606, A9TDFC610, A9TDFC613, A9TDFC616, A9TDFC625, A9TDFC632, A9TDFC640, A9TDFD606, A9TDFD610, A9TDFD616, A9TDFD620, A9TDFD625, A9TDFD632 19503 - A9TPDD610, A9TPDD613, A9TPDD616, A9TPED610, A9TPED613, A9TPED616, A9TPED625, A9TPED632, A9TPED640 19504 - A9TYAE225, A9TYAE240, A9TYBE225, A9TYBE240 19505 - A9TAA1225, A9TAA1240, A9TAA225, A9TAA2240, A9TAB1225, A9TAB1240, A9TAB2225, A9TAB2240 19506 - A9TYAE625, A9TYAE640 19507 - A9TAA1625, A9TAA1640, A9TAA2625, A9TAA2640 19508 - A9TDND606, A9TDND610, A9TDND616, A9TDND620, A9TDND625, A9TDND632, A9TDNC606, A9TDNC610, A9TDNC616, A9TDNC625, A9TDNC632, A9TDNC640 19600 - A9V6E225, A9V6E240, A9V8E225, A9V8E240, A9Y6E625, A9Y6E640, A9Y8E625, A9Y8E640 20200 - ZBRT1 20201 - ZBRT2
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the device and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79AF | 31152 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER of gateway, calculated inside the Panel Server
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B4 | 31157 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER – Maximum value between device and Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server

## TH150S
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Ambient Data | 0x0FA0 | 4001 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value
Ambient Data | 0x0FA2 | 4003 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Maximum value that the device is able to read (maximum measurable temperature).
Ambient Data | 0x0FA4 | 4005 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Minimum value that the device is able to read (minimum measurable temperature).
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Configuration | 0x792D | 31022 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the commodity of the wireless device 1. Electricity 2. Gas 3. Fuel oil 4. Air 5. Steam 6. Water 7. Environment 8. Other 9. Custom (Free text to enter): User can enter 10 custom values
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier : 16131 - LV933071W, LV933072W, LV933073W 16132 - LV947600W, LV947602W, LV947603W 17200 - A9MEM1520 17201 - A9MEM1521 17202 - A9MEM1522 17203 - A9MEM1540 17204 - A9MEM1541 17205 - A9MEM1542 17206 - A9MEM1560 17207 - A9MEM1561 17208 - A9MEM1562 17209 - A9MEM1563 17210 - A9MEM1570 17211 - A9MEM1571 17212 - A9MEM1572 17213 - A9MEM1543 17214 - A9MEM1573 17215 - A9MEM1564 17216 - A9MEM1574 17218 - A9MEM1575 17300 - EMS59440 17301 - EMS59443 17302 - A9XST114, ESST010B0400 17305 - SED-CO2-G-5045 17306 - SED-TRH-G-5045 17308 - PD100X001 17320 - SPTH150S 17321 - SPTH150M 17322 - SPTH200M 17350 - SMT10020 (V1) 17351 - SMT10020 (V2) 17660 - OVA44210, OVA44211, OVA44212, OVA44213, OVA44214, OVA44215, OVA47210, OVA47211, OVA47212, OVA47213, OVA47214, OVA47215, OVA59130, OVA59131, OVA59132, OVA59230, OVA59231, OVA59330, OVA59331, OV59430, OVA59431 17750 - LV429453 17751 - LV429454 17800 - LV434020 17801 - LV434021 17802 - LV434022 17803 - LV434023 17854 - PLTPPB1253P 17900 - A9XMC2D3 17901 - A9XMC1D3 17950 - PLTQO301P 17951 - PLTQO601P 17952 - PLTQO302P 17953 - PLTQO602P 17954 - PLTQO303P 17955 - PLTQO603P 17956 - PLTE601P 17957 - PLTE602P 17958 - PLTE603P 17969 - PLTR1203P 17970 - PLTR6003P 17971 - PLTR10003P 17972 - PLTR20003P 17973 - A9MEM1590 17974 - A9MEM1591 17975 - A9MEM1592 17976 - A9MEM1593 17980 - A9MEM1580 19500 - A9TYBE625, A9TYBE640 19501 - A9TAB1625, A9TAB1640, A9TAB2625, A9TAB2640 19502 - A9TDEC610, A9TDEC613, A9TDEC616, A9TDFC606, A9TDFC610, A9TDFC613, A9TDFC616, A9TDFC625, A9TDFC632, A9TDFC640, A9TDFD606, A9TDFD610, A9TDFD616, A9TDFD620, A9TDFD625, A9TDFD632 19503 - A9TPDD610, A9TPDD613, A9TPDD616, A9TPED610, A9TPED613, A9TPED616, A9TPED625, A9TPED632, A9TPED640 19504 - A9TYAE225, A9TYAE240, A9TYBE225, A9TYBE240 19505 - A9TAA1225, A9TAA1240, A9TAA225, A9TAA2240, A9TAB1225, A9TAB1240, A9TAB2225, A9TAB2240 19506 - A9TYAE625, A9TYAE640 19507 - A9TAA1625, A9TAA1640, A9TAA2625, A9TAA2640 19508 - A9TDND606, A9TDND610, A9TDND616, A9TDND620, A9TDND625, A9TDND632, A9TDNC606, A9TDNC610, A9TDNC616, A9TDNC625, A9TDNC632, A9TDNC640 19600 - A9V6E225, A9V6E240, A9V8E225, A9V8E240, A9Y6E625, A9Y6E640, A9Y8E625, A9Y8E640 20200 - ZBRT1 20201 - ZBRT2
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the device and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79AC | 31149 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI of the device, received by Panel Server
Diagnostic Data | 0x79AE | 31151 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Link Quality Indicator (LQI) of the device, received by Panel Server
Diagnostic Data | 0x79AF | 31152 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER of gateway, calculated inside the Panel Server
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B4 | 31157 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER – Maximum value between device and Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server

## TH150M
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Ambient Data | 0x1006 | 4103 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Phase A temperature measurement
Ambient Data | 0x1008 | 4105 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Phase B temperature measurement
Ambient Data | 0x100A | 4107 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Phase C temperature measurement
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Configuration | 0x792D | 31022 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the commodity of the wireless device 1. Electricity 2. Gas 3. Fuel oil 4. Air 5. Steam 6. Water 7. Environment 8. Other 9. Custom (Free text to enter): User can enter 10 custom values
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier : 16131 - LV933071W, LV933072W, LV933073W 16132 - LV947600W, LV947602W, LV947603W 17200 - A9MEM1520 17201 - A9MEM1521 17202 - A9MEM1522 17203 - A9MEM1540 17204 - A9MEM1541 17205 - A9MEM1542 17206 - A9MEM1560 17207 - A9MEM1561 17208 - A9MEM1562 17209 - A9MEM1563 17210 - A9MEM1570 17211 - A9MEM1571 17212 - A9MEM1572 17213 - A9MEM1543 17214 - A9MEM1573 17215 - A9MEM1564 17216 - A9MEM1574 17218 - A9MEM1575 17300 - EMS59440 17301 - EMS59443 17302 - A9XST114, ESST010B0400 17305 - SED-CO2-G-5045 17306 - SED-TRH-G-5045 17308 - PD100X001 17320 - SPTH150S 17321 - SPTH150M 17322 - SPTH200M 17350 - SMT10020 (V1) 17351 - SMT10020 (V2) 17660 - OVA44210, OVA44211, OVA44212, OVA44213, OVA44214, OVA44215, OVA47210, OVA47211, OVA47212, OVA47213, OVA47214, OVA47215, OVA59130, OVA59131, OVA59132, OVA59230, OVA59231, OVA59330, OVA59331, OV59430, OVA59431 17750 - LV429453 17751 - LV429454 17800 - LV434020 17801 - LV434021 17802 - LV434022 17803 - LV434023 17854 - PLTPPB1253P 17900 - A9XMC2D3 17901 - A9XMC1D3 17950 - PLTQO301P 17951 - PLTQO601P 17952 - PLTQO302P 17953 - PLTQO602P 17954 - PLTQO303P 17955 - PLTQO603P 17956 - PLTE601P 17957 - PLTE602P 17958 - PLTE603P 17969 - PLTR1203P 17970 - PLTR6003P 17971 - PLTR10003P 17972 - PLTR20003P 17973 - A9MEM1590 17974 - A9MEM1591 17975 - A9MEM1592 17976 - A9MEM1593 17980 - A9MEM1580 19500 - A9TYBE625, A9TYBE640 19501 - A9TAB1625, A9TAB1640, A9TAB2625, A9TAB2640 19502 - A9TDEC610, A9TDEC613, A9TDEC616, A9TDFC606, A9TDFC610, A9TDFC613, A9TDFC616, A9TDFC625, A9TDFC632, A9TDFC640, A9TDFD606, A9TDFD610, A9TDFD616, A9TDFD620, A9TDFD625, A9TDFD632 19503 - A9TPDD610, A9TPDD613, A9TPDD616, A9TPED610, A9TPED613, A9TPED616, A9TPED625, A9TPED632, A9TPED640 19504 - A9TYAE225, A9TYAE240, A9TYBE225, A9TYBE240 19505 - A9TAA1225, A9TAA1240, A9TAA225, A9TAA2240, A9TAB1225, A9TAB1240, A9TAB2225, A9TAB2240 19506 - A9TYAE625, A9TYAE640 19507 - A9TAA1625, A9TAA1640, A9TAA2625, A9TAA2640 19508 - A9TDND606, A9TDND610, A9TDND616, A9TDND620, A9TDND625, A9TDND632, A9TDNC606, A9TDNC610, A9TDNC616, A9TDNC625, A9TDNC632, A9TDNC640 19600 - A9V6E225, A9V6E240, A9V8E225, A9V8E240, A9Y6E625, A9Y6E640, A9Y8E625, A9Y8E640 20200 - ZBRT1 20201 - ZBRT2
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the device and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79AC | 31149 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI of the device, received by Panel Server
Diagnostic Data | 0x79AE | 31151 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Link Quality Indicator (LQI) of the device, received by Panel Server
Diagnostic Data | 0x79AF | 31152 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER of gateway, calculated inside the Panel Server
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B4 | 31157 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER – Maximum value between device and Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server

## TH200M
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Device Temperature Metering Data | 0x0C3B | 3132 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature
Ambient Data | 0x1004 | 4101 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Neutral temperature measurement
Ambient Data | 0x1006 | 4103 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Phase A temperature measurement
Ambient Data | 0x1008 | 4105 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Phase B temperature measurement
Ambient Data | 0x100A | 4107 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Phase C temperature measurement
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Configuration | 0x792D | 31022 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the commodity of the wireless device 1. Electricity 2. Gas 3. Fuel oil 4. Air 5. Steam 6. Water 7. Environment 8. Other 9. Custom (Free text to enter): User can enter 10 custom values
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier : 16131 - LV933071W, LV933072W, LV933073W 16132 - LV947600W, LV947602W, LV947603W 17200 - A9MEM1520 17201 - A9MEM1521 17202 - A9MEM1522 17203 - A9MEM1540 17204 - A9MEM1541 17205 - A9MEM1542 17206 - A9MEM1560 17207 - A9MEM1561 17208 - A9MEM1562 17209 - A9MEM1563 17210 - A9MEM1570 17211 - A9MEM1571 17212 - A9MEM1572 17213 - A9MEM1543 17214 - A9MEM1573 17215 - A9MEM1564 17216 - A9MEM1574 17218 - A9MEM1575 17300 - EMS59440 17301 - EMS59443 17302 - A9XST114, ESST010B0400 17305 - SED-CO2-G-5045 17306 - SED-TRH-G-5045 17308 - PD100X001 17320 - SPTH150S 17321 - SPTH150M 17322 - SPTH200M 17350 - SMT10020 (V1) 17351 - SMT10020 (V2) 17660 - OVA44210, OVA44211, OVA44212, OVA44213, OVA44214, OVA44215, OVA47210, OVA47211, OVA47212, OVA47213, OVA47214, OVA47215, OVA59130, OVA59131, OVA59132, OVA59230, OVA59231, OVA59330, OVA59331, OV59430, OVA59431 17750 - LV429453 17751 - LV429454 17800 - LV434020 17801 - LV434021 17802 - LV434022 17803 - LV434023 17854 - PLTPPB1253P 17900 - A9XMC2D3 17901 - A9XMC1D3 17950 - PLTQO301P 17951 - PLTQO601P 17952 - PLTQO302P 17953 - PLTQO602P 17954 - PLTQO303P 17955 - PLTQO603P 17956 - PLTE601P 17957 - PLTE602P 17958 - PLTE603P 17969 - PLTR1203P 17970 - PLTR6003P 17971 - PLTR10003P 17972 - PLTR20003P 17973 - A9MEM1590 17974 - A9MEM1591 17975 - A9MEM1592 17976 - A9MEM1593 17980 - A9MEM1580 19500 - A9TYBE625, A9TYBE640 19501 - A9TAB1625, A9TAB1640, A9TAB2625, A9TAB2640 19502 - A9TDEC610, A9TDEC613, A9TDEC616, A9TDFC606, A9TDFC610, A9TDFC613, A9TDFC616, A9TDFC625, A9TDFC632, A9TDFC640, A9TDFD606, A9TDFD610, A9TDFD616, A9TDFD620, A9TDFD625, A9TDFD632 19503 - A9TPDD610, A9TPDD613, A9TPDD616, A9TPED610, A9TPED613, A9TPED616, A9TPED625, A9TPED632, A9TPED640 19504 - A9TYAE225, A9TYAE240, A9TYBE225, A9TYBE240 19505 - A9TAA1225, A9TAA1240, A9TAA225, A9TAA2240, A9TAB1225, A9TAB1240, A9TAB2225, A9TAB2240 19506 - A9TYAE625, A9TYAE640 19507 - A9TAA1625, A9TAA1640, A9TAA2625, A9TAA2640 19508 - A9TDND606, A9TDND610, A9TDND616, A9TDND620, A9TDND625, A9TDND632, A9TDNC606, A9TDNC610, A9TDNC616, A9TDNC625, A9TDNC632, A9TDNC640 19600 - A9V6E225, A9V6E240, A9V8E225, A9V8E240, A9Y6E625, A9Y6E640, A9Y8E625, A9Y8E640 20200 - ZBRT1 20201 - ZBRT2
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the device and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79AC | 31149 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI of the device, received by Panel Server
Diagnostic Data | 0x79AE | 31151 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Link Quality Indicator (LQI) of the device, received by Panel Server
Diagnostic Data | 0x79AF | 31152 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER of gateway, calculated inside the Panel Server
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B4 | 31157 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER – Maximum value between device and Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server

## CL110
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Load Monitoring - Alarm | 0x0CE1 | 3298 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) – refer to register 3300 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active
Load Monitoring - Alarm | 0x0CE3 | 3300 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active
Diagnostic Data | 0x0CF3 | 3316 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Battery voltage
Ambient Data | 0x0FA0 | 4001 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value
Ambient Data | 0x0FA2 | 4003 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Maximum value that the device is able to read (maximum measurable temperature).
Ambient Data | 0x0FA4 | 4005 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Minimum value that the device is able to read (minimum measurable temperature).
Ambient Data | 0x0FA6 | 4007 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value Example: 50% represented as 0.50
Ambient Data | 0x0FA8 | 4009 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Maximum value that the device is able to read (maximum measurable humidity).
Ambient Data | 0x0FAA | 4011 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Minimum value that the device is able to read (minimum measurable humidity).
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Configuration | 0x792D | 31022 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the commodity of the wireless device 1. Electricity 2. Gas 3. Fuel oil 4. Air 5. Steam 6. Water 7. Environment 8. Other 9. Custom (Free text to enter): User can enter 10 custom values
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier : 16131 - LV933071W, LV933072W, LV933073W 16132 - LV947600W, LV947602W, LV947603W 17200 - A9MEM1520 17201 - A9MEM1521 17202 - A9MEM1522 17203 - A9MEM1540 17204 - A9MEM1541 17205 - A9MEM1542 17206 - A9MEM1560 17207 - A9MEM1561 17208 - A9MEM1562 17209 - A9MEM1563 17210 - A9MEM1570 17211 - A9MEM1571 17212 - A9MEM1572 17213 - A9MEM1543 17214 - A9MEM1573 17215 - A9MEM1564 17216 - A9MEM1574 17218 - A9MEM1575 17300 - EMS59440 17301 - EMS59443 17302 - A9XST114, ESST010B0400 17305 - SED-CO2-G-5045 17306 - SED-TRH-G-5045 17308 - PD100X001 17320 - SPTH150S 17321 - SPTH150M 17322 - SPTH200M 17350 - SMT10020 (V1) 17351 - SMT10020 (V2) 17660 - OVA44210, OVA44211, OVA44212, OVA44213, OVA44214, OVA44215, OVA47210, OVA47211, OVA47212, OVA47213, OVA47214, OVA47215, OVA59130, OVA59131, OVA59132, OVA59230, OVA59231, OVA59330, OVA59331, OV59430, OVA59431 17750 - LV429453 17751 - LV429454 17800 - LV434020 17801 - LV434021 17802 - LV434022 17803 - LV434023 17854 - PLTPPB1253P 17900 - A9XMC2D3 17901 - A9XMC1D3 17950 - PLTQO301P 17951 - PLTQO601P 17952 - PLTQO302P 17953 - PLTQO602P 17954 - PLTQO303P 17955 - PLTQO603P 17956 - PLTE601P 17957 - PLTE602P 17958 - PLTE603P 17969 - PLTR1203P 17970 - PLTR6003P 17971 - PLTR10003P 17972 - PLTR20003P 17973 - A9MEM1590 17974 - A9MEM1591 17975 - A9MEM1592 17976 - A9MEM1593 17980 - A9MEM1580 19500 - A9TYBE625, A9TYBE640 19501 - A9TAB1625, A9TAB1640, A9TAB2625, A9TAB2640 19502 - A9TDEC610, A9TDEC613, A9TDEC616, A9TDFC606, A9TDFC610, A9TDFC613, A9TDFC616, A9TDFC625, A9TDFC632, A9TDFC640, A9TDFD606, A9TDFD610, A9TDFD616, A9TDFD620, A9TDFD625, A9TDFD632 19503 - A9TPDD610, A9TPDD613, A9TPDD616, A9TPED610, A9TPED613, A9TPED616, A9TPED625, A9TPED632, A9TPED640 19504 - A9TYAE225, A9TYAE240, A9TYBE225, A9TYBE240 19505 - A9TAA1225, A9TAA1240, A9TAA225, A9TAA2240, A9TAB1225, A9TAB1240, A9TAB2225, A9TAB2240 19506 - A9TYAE625, A9TYAE640 19507 - A9TAA1625, A9TAA1640, A9TAA2625, A9TAA2640 19508 - A9TDND606, A9TDND610, A9TDND616, A9TDND620, A9TDND625, A9TDND632, A9TDNC606, A9TDNC610, A9TDNC616, A9TDNC625, A9TDNC632, A9TDNC640 19600 - A9V6E225, A9V6E240, A9V8E225, A9V8E240, A9Y6E625, A9Y6E640, A9Y8E625, A9Y8E640 20200 - ZBRT1 20201 - ZBRT2
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the device and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79AF | 31152 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER of gateway, calculated inside the Panel Server
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B4 | 31157 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER – Maximum value between device and Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server

## CO2 sensors
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Load Monitoring - Alarm | 0x0CE1 | 3298 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) – refer to register 3300 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active
Load Monitoring - Alarm | 0x0CE3 | 3300 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active
Diagnostic Data | 0x0CF3 | 3316 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Battery voltage
Ambient Data | 0x0FA0 | 4001 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value
Ambient Data | 0x0FA2 | 4003 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Maximum value that the device is able to read (maximum measurable temperature).
Ambient Data | 0x0FA4 | 4005 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Minimum value that the device is able to read (minimum measurable temperature).
Ambient Data | 0x0FA6 | 4007 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value Example: 50% represented as 0.50
Ambient Data | 0x0FA8 | 4009 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Maximum value that the device is able to read (maximum measurable humidity).
Ambient Data | 0x0FAA | 4011 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Minimum value that the device is able to read (minimum measurable humidity).
Ambient Data | 0x0FAE | 4015 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | CO2 (Example:5000 ppm represented as 0,005)
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Configuration | 0x792D | 31022 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the commodity of the wireless device 1. Electricity 2. Gas 3. Fuel oil 4. Air 5. Steam 6. Water 7. Environment 8. Other 9. Custom (Free text to enter): User can enter 10 custom values
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier : 16131 - LV933071W, LV933072W, LV933073W 16132 - LV947600W, LV947602W, LV947603W 17200 - A9MEM1520 17201 - A9MEM1521 17202 - A9MEM1522 17203 - A9MEM1540 17204 - A9MEM1541 17205 - A9MEM1542 17206 - A9MEM1560 17207 - A9MEM1561 17208 - A9MEM1562 17209 - A9MEM1563 17210 - A9MEM1570 17211 - A9MEM1571 17212 - A9MEM1572 17213 - A9MEM1543 17214 - A9MEM1573 17215 - A9MEM1564 17216 - A9MEM1574 17218 - A9MEM1575 17300 - EMS59440 17301 - EMS59443 17302 - A9XST114, ESST010B0400 17305 - SED-CO2-G-5045 17306 - SED-TRH-G-5045 17308 - PD100X001 17320 - SPTH150S 17321 - SPTH150M 17322 - SPTH200M 17350 - SMT10020 (V1) 17351 - SMT10020 (V2) 17660 - OVA44210, OVA44211, OVA44212, OVA44213, OVA44214, OVA44215, OVA47210, OVA47211, OVA47212, OVA47213, OVA47214, OVA47215, OVA59130, OVA59131, OVA59132, OVA59230, OVA59231, OVA59330, OVA59331, OV59430, OVA59431 17750 - LV429453 17751 - LV429454 17800 - LV434020 17801 - LV434021 17802 - LV434022 17803 - LV434023 17854 - PLTPPB1253P 17900 - A9XMC2D3 17901 - A9XMC1D3 17950 - PLTQO301P 17951 - PLTQO601P 17952 - PLTQO302P 17953 - PLTQO602P 17954 - PLTQO303P 17955 - PLTQO603P 17956 - PLTE601P 17957 - PLTE602P 17958 - PLTE603P 17969 - PLTR1203P 17970 - PLTR6003P 17971 - PLTR10003P 17972 - PLTR20003P 17973 - A9MEM1590 17974 - A9MEM1591 17975 - A9MEM1592 17976 - A9MEM1593 17980 - A9MEM1580 19500 - A9TYBE625, A9TYBE640 19501 - A9TAB1625, A9TAB1640, A9TAB2625, A9TAB2640 19502 - A9TDEC610, A9TDEC613, A9TDEC616, A9TDFC606, A9TDFC610, A9TDFC613, A9TDFC616, A9TDFC625, A9TDFC632, A9TDFC640, A9TDFD606, A9TDFD610, A9TDFD616, A9TDFD620, A9TDFD625, A9TDFD632 19503 - A9TPDD610, A9TPDD613, A9TPDD616, A9TPED610, A9TPED613, A9TPED616, A9TPED625, A9TPED632, A9TPED640 19504 - A9TYAE225, A9TYAE240, A9TYBE225, A9TYBE240 19505 - A9TAA1225, A9TAA1240, A9TAA225, A9TAA2240, A9TAB1225, A9TAB1240, A9TAB2225, A9TAB2240 19506 - A9TYAE625, A9TYAE640 19507 - A9TAA1625, A9TAA1640, A9TAA2625, A9TAA2640 19508 - A9TDND606, A9TDND610, A9TDND616, A9TDND620, A9TDND625, A9TDND632, A9TDNC606, A9TDNC610, A9TDNC616, A9TDNC625, A9TDNC632, A9TDNC640 19600 - A9V6E225, A9V6E240, A9V8E225, A9V8E240, A9Y6E625, A9Y6E640, A9Y8E625, A9Y8E640 20200 - ZBRT1 20201 - ZBRT2
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the device and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79AF | 31152 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER of gateway, calculated inside the Panel Server
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B4 | 31157 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER – Maximum value between device and Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server

## Temperature sensors TRH
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Load Monitoring - Alarm | 0x0CE1 | 3298 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) – refer to register 3300 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active
Load Monitoring - Alarm | 0x0CE3 | 3300 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active
Diagnostic Data | 0x0CF3 | 3316 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Battery voltage
Ambient Data | 0x0FA0 | 4001 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value
Ambient Data | 0x0FA2 | 4003 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Maximum value that the device is able to read (maximum measurable temperature).
Ambient Data | 0x0FA4 | 4005 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Minimum value that the device is able to read (minimum measurable temperature).
Ambient Data | 0x0FA6 | 4007 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value Example: 50% represented as 0.50
Ambient Data | 0x0FA8 | 4009 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Maximum value that the device is able to read (maximum measurable humidity).
Ambient Data | 0x0FAA | 4011 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Minimum value that the device is able to read (minimum measurable humidity).
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Configuration | 0x792D | 31022 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the commodity of the wireless device 1. Electricity 2. Gas 3. Fuel oil 4. Air 5. Steam 6. Water 7. Environment 8. Other 9. Custom (Free text to enter): User can enter 10 custom values
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier : 16131 - LV933071W, LV933072W, LV933073W 16132 - LV947600W, LV947602W, LV947603W 17200 - A9MEM1520 17201 - A9MEM1521 17202 - A9MEM1522 17203 - A9MEM1540 17204 - A9MEM1541 17205 - A9MEM1542 17206 - A9MEM1560 17207 - A9MEM1561 17208 - A9MEM1562 17209 - A9MEM1563 17210 - A9MEM1570 17211 - A9MEM1571 17212 - A9MEM1572 17213 - A9MEM1543 17214 - A9MEM1573 17215 - A9MEM1564 17216 - A9MEM1574 17218 - A9MEM1575 17300 - EMS59440 17301 - EMS59443 17302 - A9XST114, ESST010B0400 17305 - SED-CO2-G-5045 17306 - SED-TRH-G-5045 17308 - PD100X001 17320 - SPTH150S 17321 - SPTH150M 17322 - SPTH200M 17350 - SMT10020 (V1) 17351 - SMT10020 (V2) 17660 - OVA44210, OVA44211, OVA44212, OVA44213, OVA44214, OVA44215, OVA47210, OVA47211, OVA47212, OVA47213, OVA47214, OVA47215, OVA59130, OVA59131, OVA59132, OVA59230, OVA59231, OVA59330, OVA59331, OV59430, OVA59431 17750 - LV429453 17751 - LV429454 17800 - LV434020 17801 - LV434021 17802 - LV434022 17803 - LV434023 17854 - PLTPPB1253P 17900 - A9XMC2D3 17901 - A9XMC1D3 17950 - PLTQO301P 17951 - PLTQO601P 17952 - PLTQO302P 17953 - PLTQO602P 17954 - PLTQO303P 17955 - PLTQO603P 17956 - PLTE601P 17957 - PLTE602P 17958 - PLTE603P 17969 - PLTR1203P 17970 - PLTR6003P 17971 - PLTR10003P 17972 - PLTR20003P 17973 - A9MEM1590 17974 - A9MEM1591 17975 - A9MEM1592 17976 - A9MEM1593 17980 - A9MEM1580 19500 - A9TYBE625, A9TYBE640 19501 - A9TAB1625, A9TAB1640, A9TAB2625, A9TAB2640 19502 - A9TDEC610, A9TDEC613, A9TDEC616, A9TDFC606, A9TDFC610, A9TDFC613, A9TDFC616, A9TDFC625, A9TDFC632, A9TDFC640, A9TDFD606, A9TDFD610, A9TDFD616, A9TDFD620, A9TDFD625, A9TDFD632 19503 - A9TPDD610, A9TPDD613, A9TPDD616, A9TPED610, A9TPED613, A9TPED616, A9TPED625, A9TPED632, A9TPED640 19504 - A9TYAE225, A9TYAE240, A9TYBE225, A9TYBE240 19505 - A9TAA1225, A9TAA1240, A9TAA225, A9TAA2240, A9TAB1225, A9TAB1240, A9TAB2225, A9TAB2240 19506 - A9TYAE625, A9TYAE640 19507 - A9TAA1625, A9TAA1640, A9TAA2625, A9TAA2640 19508 - A9TDND606, A9TDND610, A9TDND616, A9TDND620, A9TDND625, A9TDND632, A9TDNC606, A9TDNC610, A9TDNC616, A9TDNC625, A9TDNC632, A9TDNC640 19600 - A9V6E225, A9V6E240, A9V8E225, A9V8E240, A9Y6E625, A9Y6E640, A9Y8E625, A9Y8E640 20200 - ZBRT1 20201 - ZBRT2
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the device and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79AF | 31152 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER of gateway, calculated inside the Panel Server
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B4 | 31157 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER – Maximum value between device and Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server

## PowerLogic HeatTag
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Device Temperature Metering Data | 0x0C3B | 3132 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature
Load Monitoring - Alarm | 0x0CE1 | 3298 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) – refer to register 3300 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active
Load Monitoring - Alarm | 0x0CE3 | 3300 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active
HeatTag Sensor | 0x0CF9 | 3322 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | HeatTag alarm type • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide)
HeatTag Sensor | 0x0CFA | 3323 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | HeatTag alarm level • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm
Ambient Data | 0x0FA0 | 4001 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value
Ambient Data | 0x0FA2 | 4003 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Maximum value that the device is able to read (maximum measurable temperature).
Ambient Data | 0x0FA4 | 4005 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Minimum value that the device is able to read (minimum measurable temperature).
Ambient Data | 0x0FA6 | 4007 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value Example: 50% represented as 0.50
Ambient Data | 0x0FA8 | 4009 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Maximum value that the device is able to read (maximum measurable humidity).
Ambient Data | 0x0FAA | 4011 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Minimum value that the device is able to read (minimum measurable humidity).
Ambient Data | 0x0FAC | 4013 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323)
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Configuration | 0x792D | 31022 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the commodity of the wireless device 1. Electricity 2. Gas 3. Fuel oil 4. Air 5. Steam 6. Water 7. Environment 8. Other 9. Custom (Free text to enter): User can enter 10 custom values
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier : 16131 - LV933071W, LV933072W, LV933073W 16132 - LV947600W, LV947602W, LV947603W 17200 - A9MEM1520 17201 - A9MEM1521 17202 - A9MEM1522 17203 - A9MEM1540 17204 - A9MEM1541 17205 - A9MEM1542 17206 - A9MEM1560 17207 - A9MEM1561 17208 - A9MEM1562 17209 - A9MEM1563 17210 - A9MEM1570 17211 - A9MEM1571 17212 - A9MEM1572 17213 - A9MEM1543 17214 - A9MEM1573 17215 - A9MEM1564 17216 - A9MEM1574 17218 - A9MEM1575 17300 - EMS59440 17301 - EMS59443 17302 - A9XST114, ESST010B0400 17305 - SED-CO2-G-5045 17306 - SED-TRH-G-5045 17308 - PD100X001 17320 - SPTH150S 17321 - SPTH150M 17322 - SPTH200M 17350 - SMT10020 (V1) 17351 - SMT10020 (V2) 17660 - OVA44210, OVA44211, OVA44212, OVA44213, OVA44214, OVA44215, OVA47210, OVA47211, OVA47212, OVA47213, OVA47214, OVA47215, OVA59130, OVA59131, OVA59132, OVA59230, OVA59231, OVA59330, OVA59331, OV59430, OVA59431 17750 - LV429453 17751 - LV429454 17800 - LV434020 17801 - LV434021 17802 - LV434022 17803 - LV434023 17854 - PLTPPB1253P 17900 - A9XMC2D3 17901 - A9XMC1D3 17950 - PLTQO301P 17951 - PLTQO601P 17952 - PLTQO302P 17953 - PLTQO602P 17954 - PLTQO303P 17955 - PLTQO603P 17956 - PLTE601P 17957 - PLTE602P 17958 - PLTE603P 17969 - PLTR1203P 17970 - PLTR6003P 17971 - PLTR10003P 17972 - PLTR20003P 17973 - A9MEM1590 17974 - A9MEM1591 17975 - A9MEM1592 17976 - A9MEM1593 17980 - A9MEM1580 19500 - A9TYBE625, A9TYBE640 19501 - A9TAB1625, A9TAB1640, A9TAB2625, A9TAB2640 19502 - A9TDEC610, A9TDEC613, A9TDEC616, A9TDFC606, A9TDFC610, A9TDFC613, A9TDFC616, A9TDFC625, A9TDFC632, A9TDFC640, A9TDFD606, A9TDFD610, A9TDFD616, A9TDFD620, A9TDFD625, A9TDFD632 19503 - A9TPDD610, A9TPDD613, A9TPDD616, A9TPED610, A9TPED613, A9TPED616, A9TPED625, A9TPED632, A9TPED640 19504 - A9TYAE225, A9TYAE240, A9TYBE225, A9TYBE240 19505 - A9TAA1225, A9TAA1240, A9TAA225, A9TAA2240, A9TAB1225, A9TAB1240, A9TAB2225, A9TAB2240 19506 - A9TYAE625, A9TYAE640 19507 - A9TAA1625, A9TAA1640, A9TAA2625, A9TAA2640 19508 - A9TDND606, A9TDND610, A9TDND616, A9TDND620, A9TDND625, A9TDND632, A9TDNC606, A9TDNC610, A9TDNC616, A9TDNC625, A9TDNC632, A9TDNC640 19600 - A9V6E225, A9V6E240, A9V8E225, A9V8E240, A9Y6E625, A9Y6E640, A9Y8E625, A9Y8E640 20200 - ZBRT1 20201 - ZBRT2
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the device and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79AC | 31149 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI of the device, received by Panel Server
Diagnostic Data | 0x79AE | 31151 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Link Quality Indicator (LQI) of the device, received by Panel Server
Diagnostic Data | 0x79AF | 31152 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER of gateway, calculated inside the Panel Server
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B4 | 31157 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER – Maximum value between device and Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server
HeatTag Sensor | 0x79C7 | 31176 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Operation mode • 0 = Test mode (0–30 minutes after HeatTag sensor is powered on • 1 = Auto-learning mode (30 minutes–8 hours after HeatTag sensor is powered on) • 2 = Normal operation mode (>8 hours after HeatTag sensor is powered on)

## Acti9 Active
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Current Metering Data | 0x0BB7 | 3000 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A
Current Metering Data | 0x0BB9 | 3002 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B
Current Metering Data | 0x0BBB | 3004 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C
Voltage Metering Data | 0x0BD3 | 3028 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N
Voltage Metering Data | 0x0BD5 | 3030 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N
Voltage Metering Data | 0x0BD7 | 3032 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N
Power Metering Data | 0x0BED | 3054 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A
Power Metering Data | 0x0BEF | 3056 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B
Power Metering Data | 0x0BF1 | 3058 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C
Power Metering Data | 0x0BF3 | 3060 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power
Power Metering Data | 0x0BF5 | 3062 | 2 | R | - | VAR | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Reactive power on phase A
Power Metering Data | 0x0BF7 | 3064 | 2 | R | - | VAR | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Reactive power on phase B
Power Metering Data | 0x0BF9 | 3066 | 2 | R | - | VAR | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Reactive power on phase C
Power Metering Data | 0x0BFB | 3068 | 2 | R | - | VAR | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power
Power Metering Data | 0x0BFD | 3070 | 2 | R | - | VA | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Apparent power on phase A
Power Metering Data | 0x0BFF | 3072 | 2 | R | - | VA | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Apparent power on phase B
Power Metering Data | 0x0C01 | 3074 | 2 | R | - | VA | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Apparent power on phase C
Power Metering Data | 0x0C03 | 3076 | 2 | R | - | VA | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic)
Power Factor Metering Data | 0x0C0B | 3084 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor
Power Factor Metering Data | 0x0C0D | 3086 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Power factor sign convention • 0 = IEC • 1 = IEEE
Device Temperature Metering Data | 0x0C3B | 3132 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature
Energy Data - Legacy Zone | 0x0C83 | 3204 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Total active energy delivered + received (not resettable)
Energy Data - Legacy Zone | 0x0CB7 | 3256 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial active energy delivered + received (resettable)
Energy Data - Legacy Zone | 0x0CBB | 3260 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial active energy counter. The value returns to zero by Panel Server.
Energy Data - Legacy Zone | 0x0CBF | 3264 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial active energy delivered (resettable)
Energy Data - Legacy Zone | 0x0CC3 | 3268 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial active energy delivered counter. The value returns to zero by Panel Server.
Energy Data - Legacy Zone | 0x0CC7 | 3272 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial active energy received (resettable)
Energy Data - Legacy Zone | 0x0CCB | 3276 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial active energy received counter. The value returns to zero by Panel Server.
Energy Data - Legacy Zone | 0x0CCF | 3280 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial reactive energy delivered (resettable)
Energy Data - Legacy Zone | 0x0CD3 | 3284 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial reactive energy delivered counter. The value returns to zero by Panel Server.
Energy Data - Legacy Zone | 0x0CD7 | 3288 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial reactive energy received (resettable)
Energy Data - Legacy Zone | 0x0CDB | 3292 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial reactive energy received counter. The value returns to zero by Panel Server.
Load Monitoring - Alarm | 0x0CE1 | 3298 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) – refer to register 3300 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active
Load Monitoring - Alarm | 0x0CE3 | 3300 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active
Load Monitoring - Alarm | 0x0CE5 | 3302 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Last RMS current measured on phase B when voltage loss occurred
Load Monitoring - Alarm | 0x0CE7 | 3304 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Last RMS current measured on phase A when voltage loss occurred
Load Monitoring - Alarm | 0x0CE9 | 3306 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Last RMS current measured on phase C when voltage loss occurred
Load Monitoring - Alarm | 0x0CF5 | 3318 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) – refer to register 3319 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm
Load Monitoring - Alarm | 0x0CF6 | 3319 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm
Load Monitoring - Alarm | 0x0CF7 | 3320 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the pre-alarm bitmap (0 = Invalid / 1 = Valid) – refer to register 3321 • Bit 0 = Validity of Overload ratio from trip threshold alarm • Bit 1 = Validity of Overvoltage ratio from trip threshold alarm • Bit 2 = Validity of Earth-Leakage ratio from trip threshold alarm
Load Monitoring - Alarm | 0x0CF8 | 3321 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Pre-alarm bitmap status (0 = Inactive / 1 = Active) • Bit 0 = Status of Overload ratio from trip threshold alarm • Bit 1 = Status of Overvoltage ratio from trip threshold alarm • Bit 2 = Status of Earth-Leakage ratio from trip threshold alarm
Alarm threshold coef (Ground Fault) | 0x0D25 | 3366 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Ground fault level
Alarm threshold coef (Overload) | 0x0D27 | 3368 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Pre-alarm on overload tripping threshold
Alarm threshold coef (Overvoltage) | 0x0D29 | 3370 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Pre-alarm on overvoltage tripping threshold
Alarm threshold coef (Earth Leakage) | 0x0D2B | 3372 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Pre-alarm on earthleakage current tripping threshold
Power Demand Data | 0x0EB5 | 3766 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power
Power Demand Data | 0x0EB9 | 3770 | 2 | R | - | W | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Peak demand total active power
Power Demand Data | 0x0EBB | 3772 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Peak demand total active power timestamp
Energy Data – New Zone | 0x1390 | 5009 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy delivered (resettable)
Energy Data – New Zone | 0x1394 | 5013 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy delivered count positively (not resettable)
Energy Data – New Zone | 0x1398 | 5017 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy received (resettable)
Energy Data – New Zone | 0x139C | 5021 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy received count negatively (not resettable)
Energy Data – New Zone | 0x13B8 | 5049 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase A delivered (resettable)
Energy Data – New Zone | 0x13BC | 5053 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase A delivered (not resettable)
Energy Data – New Zone | 0x13C0 | 5057 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase A received (resettable)
Energy Data – New Zone | 0x13C4 | 5061 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase A received (not resettable)
Energy Data – New Zone | 0x13E0 | 5089 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase B delivered (resettable)
Energy Data – New Zone | 0x13E4 | 5093 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase B delivered (not resettable)
Energy Data – New Zone | 0x13E8 | 5097 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase B received (resettable)
Energy Data – New Zone | 0x13EC | 5101 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase B received (not resettable)
Energy Data – New Zone | 0x1408 | 5129 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase C delivered (resettable)
Energy Data – New Zone | 0x140C | 5133 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase C delivered (not resettable)
Energy Data – New Zone | 0x1410 | 5137 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase C received (resettable)
Energy Data – New Zone | 0x1414 | 5141 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase C received (not resettable)
Energy Data – New Zone | 0x1438 | 5177 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy delivered (resettable)
Energy Data – New Zone | 0x143C | 5181 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy delivered count positively (not resettable)
Energy Data – New Zone | 0x1448 | 5193 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy received (resettable)
Energy Data – New Zone | 0x144C | 5197 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy received count negatively (not resettable)
Energy Data – New Zone | 0x1470 | 5233 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy on phase A delivered (resettable)
Energy Data – New Zone | 0x1474 | 5237 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy on phase A delivered (not resettable)
Energy Data – New Zone | 0x1478 | 5241 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy on phase A received (resettable)
Energy Data – New Zone | 0x147C | 5245 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy on phase A received (not resettable)
Energy Data – New Zone | 0x1498 | 5273 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy on phase B delivered (resettable)
Energy Data – New Zone | 0x149C | 5277 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy on phase B delivered (not resettable)
Energy Data – New Zone | 0x14A0 | 5281 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy on phase B received (resettable)
Energy Data – New Zone | 0x14A4 | 5285 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy on phase B received (not resettable)
Energy Data – New Zone | 0x14C0 | 5313 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy on phase C delivered (resettable)
Energy Data – New Zone | 0x14C4 | 5317 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy on phase C delivered (not resettable)
Energy Data – New Zone | 0x14C8 | 5321 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy on phase C received (resettable)
Energy Data – New Zone | 0x14CC | 5325 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy on phase C received (not resettable)
Energy Data – New Zone | 0x14F4 | 5365 | 4 | RW | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Apparent energy delivered + received (resettable)
Energy Data – New Zone | 0x14F8 | 5369 | 4 | R | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Apparent energy delivered + received (not resettable)
Energy Data – New Zone | 0x150C | 5389 | 4 | RW | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Apparent energy on phase A (resettable)
Energy Data – New Zone | 0x1510 | 5393 | 4 | R | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Apparent energy on phase A (not resettable)
Energy Data – New Zone | 0x1534 | 5429 | 4 | RW | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Apparent energy on phase B (resettable)
Energy Data – New Zone | 0x1538 | 5433 | 4 | R | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Apparent energy on phase B (not resettable)
Energy Data – New Zone | 0x155C | 5469 | 4 | RW | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Apparent energy on phase C (resettable)
Energy Data – New Zone | 0x1560 | 5473 | 4 | R | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Apparent energy on phase C (not resettable)
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Configuration | 0x7925 | 31014 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the usage of the wireless device with: • 1 = Main/Incomer • 2 = Sub/Head of group • 3 = Heating • 4 = Cooling • 5 = HVAC • 6 = Ventilation • 7 = Lighting • 8 = Office Equipment • 9 = Cooking • 10 = Food refrigeration • 11 = Elevators • 12 = Computers • 13 = Renewable power source • 14 = Genset • 15 = Compressed air • 16 = Vapor • 17 = Machine • 18 = Process • 19 = Water • 20 = Other Sockets • 21 = Other • 22 = Electrical vehicle charging station • 23 = Loads associated with renewable power source • 24 = Plug loads • 25 = Air conditionning • 26 = Domestic hot water • 27 = Heating & air conditionning • 28 = Hot sanitary water • 29 = IT • 30 = Lighting (interior) • 31 = Lighting (exterior and park) • 32 = Mixed usages • 33 = Refrigeration • 34 = Special loads • 35 = Total • 36 = Transportation system • 37 = Water system pumps • 38 = Emergency lighting
Configuration | 0x7926 | 31015 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Phase sequence with: • 1 = Phase A • 2 = Phase B • 3 = Phase C • 4 = Phase sequence ABC or AB • 5 = Phase sequence ACB or AC • 6 = Phase sequence BCA or BC • 7 = Phase sequence BAC or BA • 8 = Phase sequence CAB or CA • 9 = Phase sequence CBA or CB
Configuration | 0x7929 | 31018 | 1 | R | - | A | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Rated current of the protective device to the wireless device
Configuration | 0x792B | 31020 | 2 | R | - | V | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Rated voltage: • LN rated voltage for single phase wiring systems • LL rated voltage for 3 phases wiring systems
Configuration | 0x792D | 31022 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the commodity of the wireless device 1. Electricity 2. Gas 3. Fuel oil 4. Air 5. Steam 6. Water 7. Environment 8. Other 9. Custom (Free text to enter): User can enter 10 custom values
Configuration | 0x792E | 31023 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Reset the Peak Active Power Demand for this wireless device, Any value writen will reset Peak Active Power Demand to 0
Configuration | 0x792F | 31024 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Power supply type • 1 = Top • 2 = Bottom (default value)
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier : 16131 - LV933071W, LV933072W, LV933073W 16132 - LV947600W, LV947602W, LV947603W 17200 - A9MEM1520 17201 - A9MEM1521 17202 - A9MEM1522 17203 - A9MEM1540 17204 - A9MEM1541 17205 - A9MEM1542 17206 - A9MEM1560 17207 - A9MEM1561 17208 - A9MEM1562 17209 - A9MEM1563 17210 - A9MEM1570 17211 - A9MEM1571 17212 - A9MEM1572 17213 - A9MEM1543 17214 - A9MEM1573 17215 - A9MEM1564 17216 - A9MEM1574 17218 - A9MEM1575 17300 - EMS59440 17301 - EMS59443 17302 - A9XST114, ESST010B0400 17305 - SED-CO2-G-5045 17306 - SED-TRH-G-5045 17308 - PD100X001 17320 - SPTH150S 17321 - SPTH150M 17322 - SPTH200M 17350 - SMT10020 (V1) 17351 - SMT10020 (V2) 17660 - OVA44210, OVA44211, OVA44212, OVA44213, OVA44214, OVA44215, OVA47210, OVA47211, OVA47212, OVA47213, OVA47214, OVA47215, OVA59130, OVA59131, OVA59132, OVA59230, OVA59231, OVA59330, OVA59331, OV59430, OVA59431 17750 - LV429453 17751 - LV429454 17800 - LV434020 17801 - LV434021 17802 - LV434022 17803 - LV434023 17854 - PLTPPB1253P 17900 - A9XMC2D3 17901 - A9XMC1D3 17950 - PLTQO301P 17951 - PLTQO601P 17952 - PLTQO302P 17953 - PLTQO602P 17954 - PLTQO303P 17955 - PLTQO603P 17956 - PLTE601P 17957 - PLTE602P 17958 - PLTE603P 17969 - PLTR1203P 17970 - PLTR6003P 17971 - PLTR10003P 17972 - PLTR20003P 17973 - A9MEM1590 17974 - A9MEM1591 17975 - A9MEM1592 17976 - A9MEM1593 17980 - A9MEM1580 19500 - A9TYBE625, A9TYBE640 19501 - A9TAB1625, A9TAB1640, A9TAB2625, A9TAB2640 19502 - A9TDEC610, A9TDEC613, A9TDEC616, A9TDFC606, A9TDFC610, A9TDFC613, A9TDFC616, A9TDFC625, A9TDFC632, A9TDFC640, A9TDFD606, A9TDFD610, A9TDFD616, A9TDFD620, A9TDFD625, A9TDFD632 19503 - A9TPDD610, A9TPDD613, A9TPDD616, A9TPED610, A9TPED613, A9TPED616, A9TPED625, A9TPED632, A9TPED640 19504 - A9TYAE225, A9TYAE240, A9TYBE225, A9TYBE240 19505 - A9TAA1225, A9TAA1240, A9TAA225, A9TAA2240, A9TAB1225, A9TAB1240, A9TAB2225, A9TAB2240 19506 - A9TYAE625, A9TYAE640 19507 - A9TAA1625, A9TAA1640, A9TAA2625, A9TAA2640 19508 - A9TDND606, A9TDND610, A9TDND616, A9TDND620, A9TDND625, A9TDND632, A9TDNC606, A9TDNC610, A9TDNC616, A9TDNC625, A9TDNC632, A9TDNC640 19600 - A9V6E225, A9V6E240, A9V8E225, A9V8E240, A9Y6E625, A9Y6E640, A9Y8E625, A9Y8E640 20200 - ZBRT1 20201 - ZBRT2
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the device and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79AA | 31147 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Packet Error Rate (PER) of the device, received by Panel Server
Diagnostic Data | 0x79AC | 31149 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI of the device, received by Panel Server
Diagnostic Data | 0x79AE | 31151 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Link Quality Indicator (LQI) of the device, received by Panel Server
Diagnostic Data | 0x79AF | 31152 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER of gateway, calculated inside the Panel Server
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B4 | 31157 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER – Maximum value between device and Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server
Circuit breaker | 0x80E8 | 33001 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Circuit breaker position • 0 = Open • 1 = Close

## Wireless indication auxiliary
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Device Temperature Metering Data | 0x0C3B | 3132 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature
Load Monitoring - Alarm | 0x0CE1 | 3298 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) – refer to register 3300 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active
Load Monitoring - Alarm | 0x0CE3 | 3300 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Configuration | 0x7925 | 31014 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the usage of the wireless device with: • 1 = Main/Incomer • 2 = Sub/Head of group • 3 = Heating • 4 = Cooling • 5 = HVAC • 6 = Ventilation • 7 = Lighting • 8 = Office Equipment • 9 = Cooking • 10 = Food refrigeration • 11 = Elevators • 12 = Computers • 13 = Renewable power source • 14 = Genset • 15 = Compressed air • 16 = Vapor • 17 = Machine • 18 = Process • 19 = Water • 20 = Other Sockets • 21 = Other • 22 = Electrical vehicle charging station • 23 = Loads associated with renewable power source • 24 = Plug loads • 25 = Air conditionning • 26 = Domestic hot water • 27 = Heating & air conditionning • 28 = Hot sanitary water • 29 = IT • 30 = Lighting (interior) • 31 = Lighting (exterior and park) • 32 = Mixed usages • 33 = Refrigeration • 34 = Special loads • 35 = Total • 36 = Transportation system • 37 = Water system pumps • 38 = Emergency lighting
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier : 16131 - LV933071W, LV933072W, LV933073W 16132 - LV947600W, LV947602W, LV947603W 17200 - A9MEM1520 17201 - A9MEM1521 17202 - A9MEM1522 17203 - A9MEM1540 17204 - A9MEM1541 17205 - A9MEM1542 17206 - A9MEM1560 17207 - A9MEM1561 17208 - A9MEM1562 17209 - A9MEM1563 17210 - A9MEM1570 17211 - A9MEM1571 17212 - A9MEM1572 17213 - A9MEM1543 17214 - A9MEM1573 17215 - A9MEM1564 17216 - A9MEM1574 17218 - A9MEM1575 17300 - EMS59440 17301 - EMS59443 17302 - A9XST114, ESST010B0400 17305 - SED-CO2-G-5045 17306 - SED-TRH-G-5045 17308 - PD100X001 17320 - SPTH150S 17321 - SPTH150M 17322 - SPTH200M 17350 - SMT10020 (V1) 17351 - SMT10020 (V2) 17660 - OVA44210, OVA44211, OVA44212, OVA44213, OVA44214, OVA44215, OVA47210, OVA47211, OVA47212, OVA47213, OVA47214, OVA47215, OVA59130, OVA59131, OVA59132, OVA59230, OVA59231, OVA59330, OVA59331, OV59430, OVA59431 17750 - LV429453 17751 - LV429454 17800 - LV434020 17801 - LV434021 17802 - LV434022 17803 - LV434023 17854 - PLTPPB1253P 17900 - A9XMC2D3 17901 - A9XMC1D3 17950 - PLTQO301P 17951 - PLTQO601P 17952 - PLTQO302P 17953 - PLTQO602P 17954 - PLTQO303P 17955 - PLTQO603P 17956 - PLTE601P 17957 - PLTE602P 17958 - PLTE603P 17969 - PLTR1203P 17970 - PLTR6003P 17971 - PLTR10003P 17972 - PLTR20003P 17973 - A9MEM1590 17974 - A9MEM1591 17975 - A9MEM1592 17976 - A9MEM1593 17980 - A9MEM1580 19500 - A9TYBE625, A9TYBE640 19501 - A9TAB1625, A9TAB1640, A9TAB2625, A9TAB2640 19502 - A9TDEC610, A9TDEC613, A9TDEC616, A9TDFC606, A9TDFC610, A9TDFC613, A9TDFC616, A9TDFC625, A9TDFC632, A9TDFC640, A9TDFD606, A9TDFD610, A9TDFD616, A9TDFD620, A9TDFD625, A9TDFD632 19503 - A9TPDD610, A9TPDD613, A9TPDD616, A9TPED610, A9TPED613, A9TPED616, A9TPED625, A9TPED632, A9TPED640 19504 - A9TYAE225, A9TYAE240, A9TYBE225, A9TYBE240 19505 - A9TAA1225, A9TAA1240, A9TAA225, A9TAA2240, A9TAB1225, A9TAB1240, A9TAB2225, A9TAB2240 19506 - A9TYAE625, A9TYAE640 19507 - A9TAA1625, A9TAA1640, A9TAA2625, A9TAA2640 19508 - A9TDND606, A9TDND610, A9TDND616, A9TDND620, A9TDND625, A9TDND632, A9TDNC606, A9TDNC610, A9TDNC616, A9TDNC625, A9TDNC632, A9TDNC640 19600 - A9V6E225, A9V6E240, A9V8E225, A9V8E240, A9Y6E625, A9Y6E640, A9Y8E625, A9Y8E640 20200 - ZBRT1 20201 - ZBRT2
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the device and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79AA | 31147 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Packet Error Rate (PER) of the device, received by Panel Server
Diagnostic Data | 0x79AC | 31149 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI of the device, received by Panel Server
Diagnostic Data | 0x79AE | 31151 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Link Quality Indicator (LQI) of the device, received by Panel Server
Diagnostic Data | 0x79AF | 31152 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER of gateway, calculated inside the Panel Server
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B4 | 31157 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER – Maximum value between device and Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server
Circuit breaker | 0x80E8 | 33001 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Circuit breaker position • 0 = Open • 1 = Close
Circuit breaker | 0x80E9 | 33002 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Circuit breaker trip indicator • 0 = Off • 1 = On
Circuit breaker | 0x80EA | 33003 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Circuit breaker trip electrical fault indicator • 0 = Off • 1 = On
Digital Input | 0x84E7 | 34024 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Digital Input 1 circuit identifier
Digital Input | 0x84EC | 34029 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Features assigned to digital input 0 None 1 Custom 2 Circuit breaker status 3 Trip fault (SD) 4 Trip indicator synthesis 5 Trip elec fault (SDE) 6 Trip thermal fault (SDT) 7 Earth leakage fault 8 Ground fault 9 Surge arrester fault 10 Insulation fault 11 Circuit Breaker connected position 12 Circuit Breaker disconnected position 13 Circuit Breaker test position 14 Energy Reduction Maintenance Setting status 15 Door status 17 Drawer connected position 18 Drawer disconnected position 19 Drawer test position 20 Voltage loss 21 Advanced protection 22 Switch position 23 Fuse blown 24 Relay status 25 Trip circuit supervision 26 Emergency stop 27 Watchdog status 28 Source change over - A (Alternate) status 29 Source change over - Off status 30 Source change over - N (Normal) status 31 Motor preheating 32 Motor run 33 Motor start 34 Forced freewheel stop 35 Battery status 36 Battery end of autonomy 37 UPS status 38 UPS running mode 39 Auxiliary supply status 40 Tariff 1 Status 41 Tariff 2 Status 42 Tariff 3 Status 43 Tariff 4 Status 44 Tariff 5 Status 45 Flood detection 46 Under temperature 47 Over temperature 48 Process mode 49 Equipment status 50 Fan status 51 Standard Input Low-High 52 Standard Input 0V-24V 53 Standard Input Disconnected-Off 54 Standard input
Digital Input | 0x84F8 | 34041 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Digital Input 1 electrical status. Indicates the electrical status of the input, regardless of the assignment reference & polarity • 0 = Low level • 1 = High level
Digital input | 0x8510 | 34065 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 (takes into account the configured polarity) ENUM { ON = 1, //Active OFF = 0, //Inactive Undetermined = 65535 //Invalid value }

## Partial Discharge Box
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier : 16131 - LV933071W, LV933072W, LV933073W 16132 - LV947600W, LV947602W, LV947603W 17200 - A9MEM1520 17201 - A9MEM1521 17202 - A9MEM1522 17203 - A9MEM1540 17204 - A9MEM1541 17205 - A9MEM1542 17206 - A9MEM1560 17207 - A9MEM1561 17208 - A9MEM1562 17209 - A9MEM1563 17210 - A9MEM1570 17211 - A9MEM1571 17212 - A9MEM1572 17213 - A9MEM1543 17214 - A9MEM1573 17215 - A9MEM1564 17216 - A9MEM1574 17218 - A9MEM1575 17300 - EMS59440 17301 - EMS59443 17302 - A9XST114, ESST010B0400 17305 - SED-CO2-G-5045 17306 - SED-TRH-G-5045 17308 - PD100X001 17320 - SPTH150S 17321 - SPTH150M 17322 - SPTH200M 17350 - SMT10020 (V1) 17351 - SMT10020 (V2) 17660 - OVA44210, OVA44211, OVA44212, OVA44213, OVA44214, OVA44215, OVA47210, OVA47211, OVA47212, OVA47213, OVA47214, OVA47215, OVA59130, OVA59131, OVA59132, OVA59230, OVA59231, OVA59330, OVA59331, OV59430, OVA59431 17750 - LV429453 17751 - LV429454 17800 - LV434020 17801 - LV434021 17802 - LV434022 17803 - LV434023 17854 - PLTPPB1253P 17900 - A9XMC2D3 17901 - A9XMC1D3 17950 - PLTQO301P 17951 - PLTQO601P 17952 - PLTQO302P 17953 - PLTQO602P 17954 - PLTQO303P 17955 - PLTQO603P 17956 - PLTE601P 17957 - PLTE602P 17958 - PLTE603P 17969 - PLTR1203P 17970 - PLTR6003P 17971 - PLTR10003P 17972 - PLTR20003P 17973 - A9MEM1590 17974 - A9MEM1591 17975 - A9MEM1592 17976 - A9MEM1593 17980 - A9MEM1580 19500 - A9TYBE625, A9TYBE640 19501 - A9TAB1625, A9TAB1640, A9TAB2625, A9TAB2640 19502 - A9TDEC610, A9TDEC613, A9TDEC616, A9TDFC606, A9TDFC610, A9TDFC613, A9TDFC616, A9TDFC625, A9TDFC632, A9TDFC640, A9TDFD606, A9TDFD610, A9TDFD616, A9TDFD620, A9TDFD625, A9TDFD632 19503 - A9TPDD610, A9TPDD613, A9TPDD616, A9TPED610, A9TPED613, A9TPED616, A9TPED625, A9TPED632, A9TPED640 19504 - A9TYAE225, A9TYAE240, A9TYBE225, A9TYBE240 19505 - A9TAA1225, A9TAA1240, A9TAA225, A9TAA2240, A9TAB1225, A9TAB1240, A9TAB2225, A9TAB2240 19506 - A9TYAE625, A9TYAE640 19507 - A9TAA1625, A9TAA1640, A9TAA2625, A9TAA2640 19508 - A9TDND606, A9TDND610, A9TDND616, A9TDND620, A9TDND625, A9TDND632, A9TDNC606, A9TDNC610, A9TDNC616, A9TDNC625, A9TDNC632, A9TDNC640 19600 - A9V6E225, A9V6E240, A9V8E225, A9V8E240, A9Y6E625, A9Y6E640, A9Y8E625, A9Y8E640 20200 - ZBRT1 20201 - ZBRT2
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the device and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79AC | 31149 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI of the device, received by Panel Server
Diagnostic Data | 0x79AE | 31151 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Link Quality Indicator (LQI) of the device, received by Panel Server
Diagnostic Data | 0x79AF | 31152 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER of gateway, calculated inside the Panel Server
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B4 | 31157 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER – Maximum value between device and Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server

## PowerTagCIO
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier : 16131 - LV933071W, LV933072W, LV933073W 16132 - LV947600W, LV947602W, LV947603W 17200 - A9MEM1520 17201 - A9MEM1521 17202 - A9MEM1522 17203 - A9MEM1540 17204 - A9MEM1541 17205 - A9MEM1542 17206 - A9MEM1560 17207 - A9MEM1561 17208 - A9MEM1562 17209 - A9MEM1563 17210 - A9MEM1570 17211 - A9MEM1571 17212 - A9MEM1572 17213 - A9MEM1543 17214 - A9MEM1573 17215 - A9MEM1564 17216 - A9MEM1574 17218 - A9MEM1575 17300 - EMS59440 17301 - EMS59443 17302 - A9XST114, ESST010B0400 17305 - SED-CO2-G-5045 17306 - SED-TRH-G-5045 17308 - PD100X001 17320 - SPTH150S 17321 - SPTH150M 17322 - SPTH200M 17350 - SMT10020 (V1) 17351 - SMT10020 (V2) 17660 - OVA44210, OVA44211, OVA44212, OVA44213, OVA44214, OVA44215, OVA47210, OVA47211, OVA47212, OVA47213, OVA47214, OVA47215, OVA59130, OVA59131, OVA59132, OVA59230, OVA59231, OVA59330, OVA59331, OV59430, OVA59431 17750 - LV429453 17751 - LV429454 17800 - LV434020 17801 - LV434021 17802 - LV434022 17803 - LV434023 17854 - PLTPPB1253P 17900 - A9XMC2D3 17901 - A9XMC1D3 17950 - PLTQO301P 17951 - PLTQO601P 17952 - PLTQO302P 17953 - PLTQO602P 17954 - PLTQO303P 17955 - PLTQO603P 17956 - PLTE601P 17957 - PLTE602P 17958 - PLTE603P 17969 - PLTR1203P 17970 - PLTR6003P 17971 - PLTR10003P 17972 - PLTR20003P 17973 - A9MEM1590 17974 - A9MEM1591 17975 - A9MEM1592 17976 - A9MEM1593 17980 - A9MEM1580 19500 - A9TYBE625, A9TYBE640 19501 - A9TAB1625, A9TAB1640, A9TAB2625, A9TAB2640 19502 - A9TDEC610, A9TDEC613, A9TDEC616, A9TDFC606, A9TDFC610, A9TDFC613, A9TDFC616, A9TDFC625, A9TDFC632, A9TDFC640, A9TDFD606, A9TDFD610, A9TDFD616, A9TDFD620, A9TDFD625, A9TDFD632 19503 - A9TPDD610, A9TPDD613, A9TPDD616, A9TPED610, A9TPED613, A9TPED616, A9TPED625, A9TPED632, A9TPED640 19504 - A9TYAE225, A9TYAE240, A9TYBE225, A9TYBE240 19505 - A9TAA1225, A9TAA1240, A9TAA225, A9TAA2240, A9TAB1225, A9TAB1240, A9TAB2225, A9TAB2240 19506 - A9TYAE625, A9TYAE640 19507 - A9TAA1625, A9TAA1640, A9TAA2625, A9TAA2640 19508 - A9TDND606, A9TDND610, A9TDND616, A9TDND620, A9TDND625, A9TDND632, A9TDNC606, A9TDNC610, A9TDNC616, A9TDNC625, A9TDNC632, A9TDNC640 19600 - A9V6E225, A9V6E240, A9V8E225, A9V8E240, A9Y6E625, A9Y6E640, A9Y8E625, A9Y8E640 20200 - ZBRT1 20201 - ZBRT2
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the device and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79AA | 31147 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Packet Error Rate (PER) of the device, received by Panel Server
Diagnostic Data | 0x79AC | 31149 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI of the device, received by Panel Server
Diagnostic Data | 0x79AE | 31151 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Link Quality Indicator (LQI) of the device, received by Panel Server
Diagnostic Data | 0x79AF | 31152 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER of gateway, calculated inside the Panel Server
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B4 | 31157 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER – Maximum value between device and Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server
Digital Input | 0x84D0 | 34001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Digital Input 1 name
Digital Input | 0x84E7 | 34024 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Digital Input 1 circuit identifier
Digital Input | 0x84EA | 34027 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the usage of the device connected on DI1 of the wireless device : • 1 = Main/Incomer • 2 = Sub/Head of group • 3 = Heating • 4 = Cooling • 5 = HVAC • 6 = Ventilation • 7 = Lighting • 8 = Office Equipment • 9 = Cooking • 10 = Food refrigeration • 11 = Elevators • 12 = Computers • 13 = Renewable power source • 14 = Genset • 15 = Compressed air • 16 = Vapor • 17 = Machine • 18 = Process • 19 = Water • 20 = Other Sockets • 21 = Other • 22 = Electrical vehicle charging station • 23 = Loads associated with renewable power source • 24 = Plug loads • 25 = Air conditionning • 26 = Domestic hot water • 27 = Heating and air conditionning • 28 = Hot sanitary water • 29 = IT • 30 = Lighting (interior) • 31 = Lighting (exterior and park) • 32 = Mixed usages • 33 = Refrigeration • 34 = Special loads • 35 = Total • 36 = Transportation system • 37 = Water system pumps • 38 = Emergency lighting
Digital Input | 0x84EC | 34029 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Features assigned to digital input 0 None 1 Custom 2 Circuit breaker status 3 Trip fault (SD) 4 Trip indicator synthesis 5 Trip elec fault (SDE) 6 Trip thermal fault (SDT) 7 Earth leakage fault 8 Ground fault 9 Surge arrester fault 10 Insulation fault 11 Circuit Breaker connected position 12 Circuit Breaker disconnected position 13 Circuit Breaker test position 14 Energy Reduction Maintenance Setting status 15 Door status 17 Drawer connected position 18 Drawer disconnected position 19 Drawer test position 20 Voltage loss 21 Advanced protection 22 Switch position 23 Fuse blown 24 Relay status 25 Trip circuit supervision 26 Emergency stop 27 Watchdog status 28 Source change over - A (Alternate) status 29 Source change over - Off status 30 Source change over - N (Normal) status 31 Motor preheating 32 Motor run 33 Motor start 34 Forced freewheel stop 35 Battery status 36 Battery end of autonomy 37 UPS status 38 UPS running mode 39 Auxiliary supply status 40 Tariff 1 Status 41 Tariff 2 Status 42 Tariff 3 Status 43 Tariff 4 Status 44 Tariff 5 Status 45 Flood detection 46 Under temperature 47 Over temperature 48 Process mode 49 Equipment status 50 Fan status 51 Standard Input Low-High 52 Standard Input 0V-24V 53 Standard Input Disconnected-Off 54 Standard input
Digital Input | 0x84ED | 34030 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Polarity of the Digital Input 1 Meaning of input: /0 for inactive/1 for active/: // Input Electrical status = 0V --> input is inactive (eg: Trip fault (SD) = ‘No Fault’ / Motor run = ‘Off’) // // Input Electrical status = 230V or 24V --> input is active (eg: Trip fault (SD) = ‘Fault’ / Motor run = ‘Run’) // or Meaning of input: /1 for inactive/0 for active/ // Input Electrical status = 0V --> input is active (eg: Trip fault (SD) = ‘Fault’ / Motor run = ‘Run’) // // Input Electrical status = 230V or 24 V --> input is inactive (eg: Trip fault (SD) = ‘No Fault’ / Motor run = ‘Off’) //
Digital Input | 0x84F8 | 34041 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Digital Input 1 electrical status. Indicates the electrical status of the input, regardless of the assignment reference & polarity • 0 = Low level • 1 = High level
Digital input | 0x84FE | 34047 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position - Only available if input assigned to OF (case = 2) ENUM { Open= 0, Closed = 1 Undetermined = 65535 // Invalid value } CircuitPositionID
Digital input | 0x8508 | 34057 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip ENUM { ON = 0, // Tripped OFF = 1 // Not tripped Undetermined = 65535 // Invalid value } Status
Digital input | 0x8510 | 34065 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 (takes into account the configured polarity) ENUM { ON = 1, //Active OFF = 0, //Inactive Undetermined = 65535 //Invalid value }
Digital input | 0x8598 | 34201 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text giving the context of use of the Digital Input 1 when Digital Input 1 is defined as 'Custom'
Digital input | 0x85A2 | 34211 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text defining the inactive value of the Digital Input 1 when the Digital Input 1 is defined as 'Custom'
Digital input | 0x85AC | 34221 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text defining the active value of the Digital Input 1 when the Digital Input 1 is defined as 'Custom'
Digital output | 0x9088 | 37001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Name given by the user to the Digital Output. Can be used for the name of the asset controled by the DO, or to specify the user define connected product and/or the user defined output assignment. Maximum 20 Characters Name should be wriiten from MSB to LSB
Digital output | 0x909F | 37024 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Name of the circuit on witch the Output is wired. Max 5 Char. May be left empty if not applicable. The LSB of the last register will contain the 5th characters
Digital output | 0x90A2 | 37027 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the usage of the device connected on DO1 of the wireless device: • 1 = Main/Incomer • 2 = Sub/Head of group • 3 = Heating • 4 = Cooling • 5 = HVAC • 6 = Ventilation • 7 = Lighting • 8 = Office Equipment • 9 = Cooking • 10 = Food refrigeration • 11 = Elevators • 12 = Computers • 13 = Renewable power source • 14 = Genset • 15 = Compressed air • 16 = Vapor • 17 = Machine • 18 = Process • 19 = Water • 20 = Other Sockets • 21 = Other • 22 = Electrical vehicle charging station • 23 = Loads associated with renewable power source • 24 = Plug loads • 25 = Air conditionning • 26 = Domestic hot water • 27 = Heating and air conditionning • 28 = Hot sanitary water • 29 = IT • 30 = Lighting (interior) • 31 = Lighting (exterior and park) • 32 = Mixed usages • 33 = Refrigeration • 34 = Special loads • 35 = Total • 36 = Transportation system • 37 = Water system pumps • 38 = Emergency lighting
Digital output | 0x90A4 | 37029 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | ENUM { Normal = 0, // Contactor Latched = 1, // Impulse Relay (Other values reserved) } OutputBehavior
Digital output | 0x90A7 | 37032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | ENUM { Normally Open = 0, Normally Closed = 1, } DIContactTypeID
Digital output | 0x90A9 | 37034 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | ENUM { Disable = 0, Enable = 1 }
Digital output | 0x90AB | 37036 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | When Feedback loop is enabled, feedback data are available in Input 1 registers ENUM { Disable = 0, Enable = 1 // Enable is forced when Output is configured in latched mode (impulse relay) see register OutputBehavior }
Digital output | 0x90AC | 37037 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Features assigned to output: 0 None 1 Custom 2 Circuit breaker status 22 Switch position 32 Motor run 54 StandardOutput
Digital output | 0x90BA | 37051 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | ENUM { No command = 0 OffCommand = 1, // Switch to output logical state Off. Accepted only if Output is configured as Normal mode (contactor) see register OutputBehavior OnCommand = 2, // Switch to output logical state On. Accepted only if Output is configured as Normal mode (contactor) see register OutputBehavior ToggleCommand=3, // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay) see register OutputBehavior. Toggle can be used for Normal mode too }
Digital output | 0x90BB | 37052 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Output - Only significant if Output is configured as Normal mode (contactor) see register OutputBehavior. Otherwise it is set to invalid value ENUM { OFF = 0 ON = 1, Undetermined = 65535 // Invalid value }
Digital output | 0x90EC | 37101 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text giving the context of use of the Digital Input 1 when Digital Output 1 is defined as 'Custom'
Digital output | 0x90F6 | 37111 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text defining the inactive value of the Digital Input 1 when the Digital Output 1 is defined as 'Custom'
Digital output | 0x9100 | 37121 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text defining the active value of the Digital Input 1 when the Digital Output 1 is defined as 'Custom'

## PowerTagC2DI
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier : 16131 - LV933071W, LV933072W, LV933073W 16132 - LV947600W, LV947602W, LV947603W 17200 - A9MEM1520 17201 - A9MEM1521 17202 - A9MEM1522 17203 - A9MEM1540 17204 - A9MEM1541 17205 - A9MEM1542 17206 - A9MEM1560 17207 - A9MEM1561 17208 - A9MEM1562 17209 - A9MEM1563 17210 - A9MEM1570 17211 - A9MEM1571 17212 - A9MEM1572 17213 - A9MEM1543 17214 - A9MEM1573 17215 - A9MEM1564 17216 - A9MEM1574 17218 - A9MEM1575 17300 - EMS59440 17301 - EMS59443 17302 - A9XST114, ESST010B0400 17305 - SED-CO2-G-5045 17306 - SED-TRH-G-5045 17308 - PD100X001 17320 - SPTH150S 17321 - SPTH150M 17322 - SPTH200M 17350 - SMT10020 (V1) 17351 - SMT10020 (V2) 17660 - OVA44210, OVA44211, OVA44212, OVA44213, OVA44214, OVA44215, OVA47210, OVA47211, OVA47212, OVA47213, OVA47214, OVA47215, OVA59130, OVA59131, OVA59132, OVA59230, OVA59231, OVA59330, OVA59331, OV59430, OVA59431 17750 - LV429453 17751 - LV429454 17800 - LV434020 17801 - LV434021 17802 - LV434022 17803 - LV434023 17854 - PLTPPB1253P 17900 - A9XMC2D3 17901 - A9XMC1D3 17950 - PLTQO301P 17951 - PLTQO601P 17952 - PLTQO302P 17953 - PLTQO602P 17954 - PLTQO303P 17955 - PLTQO603P 17956 - PLTE601P 17957 - PLTE602P 17958 - PLTE603P 17969 - PLTR1203P 17970 - PLTR6003P 17971 - PLTR10003P 17972 - PLTR20003P 17973 - A9MEM1590 17974 - A9MEM1591 17975 - A9MEM1592 17976 - A9MEM1593 17980 - A9MEM1580 19500 - A9TYBE625, A9TYBE640 19501 - A9TAB1625, A9TAB1640, A9TAB2625, A9TAB2640 19502 - A9TDEC610, A9TDEC613, A9TDEC616, A9TDFC606, A9TDFC610, A9TDFC613, A9TDFC616, A9TDFC625, A9TDFC632, A9TDFC640, A9TDFD606, A9TDFD610, A9TDFD616, A9TDFD620, A9TDFD625, A9TDFD632 19503 - A9TPDD610, A9TPDD613, A9TPDD616, A9TPED610, A9TPED613, A9TPED616, A9TPED625, A9TPED632, A9TPED640 19504 - A9TYAE225, A9TYAE240, A9TYBE225, A9TYBE240 19505 - A9TAA1225, A9TAA1240, A9TAA225, A9TAA2240, A9TAB1225, A9TAB1240, A9TAB2225, A9TAB2240 19506 - A9TYAE625, A9TYAE640 19507 - A9TAA1625, A9TAA1640, A9TAA2625, A9TAA2640 19508 - A9TDND606, A9TDND610, A9TDND616, A9TDND620, A9TDND625, A9TDND632, A9TDNC606, A9TDNC610, A9TDNC616, A9TDNC625, A9TDNC632, A9TDNC640 19600 - A9V6E225, A9V6E240, A9V8E225, A9V8E240, A9Y6E625, A9Y6E640, A9Y8E625, A9Y8E640 20200 - ZBRT1 20201 - ZBRT2
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the device and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79AA | 31147 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Packet Error Rate (PER) of the device, received by Panel Server
Diagnostic Data | 0x79AC | 31149 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI of the device, received by Panel Server
Diagnostic Data | 0x79AE | 31151 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Link Quality Indicator (LQI) of the device, received by Panel Server
Diagnostic Data | 0x79AF | 31152 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER of gateway, calculated inside the Panel Server
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B4 | 31157 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER – Maximum value between device and Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server
Digital Input | 0x84D0 | 34001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Digital Input 1 name
Digital Input | 0x84E7 | 34024 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Digital Input 1 circuit identifier
Digital Input | 0x84EA | 34027 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the usage of the device connected on DI1 of the wireless device : • 1 = Main/Incomer • 2 = Sub/Head of group • 3 = Heating • 4 = Cooling • 5 = HVAC • 6 = Ventilation • 7 = Lighting • 8 = Office Equipment • 9 = Cooking • 10 = Food refrigeration • 11 = Elevators • 12 = Computers • 13 = Renewable power source • 14 = Genset • 15 = Compressed air • 16 = Vapor • 17 = Machine • 18 = Process • 19 = Water • 20 = Other Sockets • 21 = Other • 22 = Electrical vehicle charging station • 23 = Loads associated with renewable power source • 24 = Plug loads • 25 = Air conditionning • 26 = Domestic hot water • 27 = Heating and air conditionning • 28 = Hot sanitary water • 29 = IT • 30 = Lighting (interior) • 31 = Lighting (exterior and park) • 32 = Mixed usages • 33 = Refrigeration • 34 = Special loads • 35 = Total • 36 = Transportation system • 37 = Water system pumps • 38 = Emergency lighting
Digital Input | 0x84EC | 34029 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Features assigned to digital input 0 None 1 Custom 2 Circuit breaker status 3 Trip fault (SD) 4 Trip indicator synthesis 5 Trip elec fault (SDE) 6 Trip thermal fault (SDT) 7 Earth leakage fault 8 Ground fault 9 Surge arrester fault 10 Insulation fault 11 Circuit Breaker connected position 12 Circuit Breaker disconnected position 13 Circuit Breaker test position 14 Energy Reduction Maintenance Setting status 15 Door status 17 Drawer connected position 18 Drawer disconnected position 19 Drawer test position 20 Voltage loss 21 Advanced protection 22 Switch position 23 Fuse blown 24 Relay status 25 Trip circuit supervision 26 Emergency stop 27 Watchdog status 28 Source change over - A (Alternate) status 29 Source change over - Off status 30 Source change over - N (Normal) status 31 Motor preheating 32 Motor run 33 Motor start 34 Forced freewheel stop 35 Battery status 36 Battery end of autonomy 37 UPS status 38 UPS running mode 39 Auxiliary supply status 40 Tariff 1 Status 41 Tariff 2 Status 42 Tariff 3 Status 43 Tariff 4 Status 44 Tariff 5 Status 45 Flood detection 46 Under temperature 47 Over temperature 48 Process mode 49 Equipment status 50 Fan status 51 Standard Input Low-High 52 Standard Input 0V-24V 53 Standard Input Disconnected-Off 54 Standard input
Digital Input | 0x84ED | 34030 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Polarity of the Digital Input 1 Meaning of input: /0 for inactive/1 for active/: // Input Electrical status = 0V --> input is inactive (eg: Trip fault (SD) = ‘No Fault’ / Motor run = ‘Off’) // // Input Electrical status = 230V or 24V --> input is active (eg: Trip fault (SD) = ‘Fault’ / Motor run = ‘Run’) // or Meaning of input: /1 for inactive/0 for active/ // Input Electrical status = 0V --> input is active (eg: Trip fault (SD) = ‘Fault’ / Motor run = ‘Run’) // // Input Electrical status = 230V or 24 V --> input is inactive (eg: Trip fault (SD) = ‘No Fault’ / Motor run = ‘Off’) //
Digital Input | 0x84F8 | 34041 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Digital Input 1 electrical status. Indicates the electrical status of the input, regardless of the assignment reference & polarity • 0 = Low level • 1 = High level
Digital input | 0x84FE | 34047 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position - Only available if input assigned to OF (case = 2) ENUM { Open= 0, Closed = 1 Undetermined = 65535 // Invalid value } CircuitPositionID
Digital input | 0x8508 | 34057 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip ENUM { ON = 0, // Tripped OFF = 1 // Not tripped Undetermined = 65535 // Invalid value } Status
Digital input | 0x8510 | 34065 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 (takes into account the configured polarity) ENUM { ON = 1, //Active OFF = 0, //Inactive Undetermined = 65535 //Invalid value }
Digital input | 0x8534 | 34101 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Digital Input 2 name
Digital input | 0x854B | 34124 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Digital Input 2 circuit identifier
Digital input | 0x854E | 34127 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the usage of the device connected on DI2 of the wireless device : • 1 = Main/Incomer • 2 = Sub/Head of group • 3 = Heating • 4 = Cooling • 5 = HVAC • 6 = Ventilation • 7 = Lighting • 8 = Office Equipment • 9 = Cooking • 10 = Food refrigeration • 11 = Elevators • 12 = Computers • 13 = Renewable power source • 14 = Genset • 15 = Compressed air • 16 = Vapor • 17 = Machine • 18 = Process • 19 = Water • 20 = Other Sockets • 21 = Other • 22 = Electrical vehicle charging station • 23 = Loads associated with renewable power source • 24 = Plug loads • 25 = Air conditionning • 26 = Domestic hot water • 27 = Heating and air conditionning • 28 = Hot sanitary water • 29 = IT • 30 = Lighting (interior) • 31 = Lighting (exterior and park) • 32 = Mixed usages • 33 = Refrigeration • 34 = Special loads • 35 = Total • 36 = Transportation system • 37 = Water system pumps • 38 = Emergency lighting
Digital input | 0x8550 | 34129 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Features assigned to digital input 0 None 1 Custom 2 Circuit breaker status 3 Trip fault (SD) 4 Trip indicator synthesis 5 Trip elec fault (SDE) 6 Trip thermal fault (SDT) 7 Earth leakage fault 8 Ground fault 9 Surge arrester fault 10 Insulation fault 11 Circuit Breaker connected position 12 Circuit Breaker disconnected position 13 Circuit Breaker test position 14 Energy Reduction Maintenance Setting status 15 Door status 17 Drawer connected position 18 Drawer disconnected position 19 Drawer test position 20 Voltage loss 21 Advanced protection 22 Switch position 23 Fuse blown 24 Relay status 25 Trip circuit supervision 26 Emergency stop 27 Watchdog status 28 Source change over - A (Alternate) status 29 Source change over - Off status 30 Source change over - N (Normal) status 31 Motor preheating 32 Motor run 33 Motor start 34 Forced freewheel stop 35 Battery status 36 Battery end of autonomy 37 UPS status 38 UPS running mode 39 Auxiliary supply status 40 Tariff 1 Status 41 Tariff 2 Status 42 Tariff 3 Status 43 Tariff 4 Status 44 Tariff 5 Status 45 Flood detection 46 Under temperature 47 Over temperature 48 Process mode 49 Equipment status 50 Fan status 51 Standard Input Low-High 52 Standard Input 0V-24V 53 Standard Input Disconnected-Off 54 Standard input
Digital input | 0x8551 | 34130 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Polarity of the Digital Input 2 Meaning of input: /0 for inactive/1 for active/: // Input Electrical status = 0V --> input is inactive (eg: Trip fault (SD) = ‘No Fault’ / Motor run = ‘Off’) // // Input Electrical status = 230V or 24V --> input is active (eg: Trip fault (SD) = ‘Fault’ / Motor run = ‘Run’) // or Meaning of input: /1 for inactive/0 for active/ // Input Electrical status = 0V --> input is active (eg: Trip fault (SD) = ‘Fault’ / Motor run = ‘Run’) // // Input Electrical status = 230V or 24 V --> input is inactive (eg: Trip fault (SD) = ‘No Fault’ / Motor run = ‘Off’) //
Digital input | 0x855C | 34141 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Digital Input 2 electrical status. Indicates the electrical status of the input, regardless of the assignment reference & polarity • 0 = Low level • 1 = High level
Digital input | 0x8562 | 34147 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position - Only available if input assigned to OF (case = 2) ENUM { Open= 0, Closed = 1 Undetermined = 65535 // Invalid value } CircuitPositionID
Digital input | 0x856C | 34157 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip ENUM { ON = 0, // Tripped OFF = 1 // Not tripped Undetermined = 65535 // Invalid value } Status
Digital input | 0x8574 | 34165 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Logical status of the Digital Input 2 (takes into account the configured polarity) ON // Active OFF // Inactive Undetermined // Invalid value
Digital input | 0x8598 | 34201 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text giving the context of use of the Digital Input 1 when Digital Input 1 is defined as 'Custom'
Digital input | 0x85A2 | 34211 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text defining the inactive value of the Digital Input 1 when the Digital Input 1 is defined as 'Custom'
Digital input | 0x85AC | 34221 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text defining the active value of the Digital Input 1 when the Digital Input 1 is defined as 'Custom'
Digital input | 0x8660 | 34401 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text giving the context of use of the Digital Input 2 when Digital Input 2 is defined as 'Custom'
Digital input | 0x866A | 34411 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text defining the inactive value of the Digital Input 2 when the Digital Input 2 is defined as 'Custom'
Digital input | 0x8674 | 34421 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text defining the active value of the Digital Input 2 when the Digital Input 2 is defined as 'Custom'

## MasterPacT MTZ Active A
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Current Metering Data | 0x0BB7 | 3000 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A
Current Metering Data | 0x0BB9 | 3002 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B
Current Metering Data | 0x0BBB | 3004 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C
Current Metering Data | 0x0BBD | 3006 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral
Current Metering Data | 0x0BBF | 3008 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on ground or earth-leakage
Load Monitoring - Alarm | 0x0CE1 | 3298 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) – refer to register 3300 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active
Load Monitoring - Alarm | 0x0CE3 | 3300 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active
Load Monitoring - Alarm | 0x0CF5 | 3318 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) – refer to register 3319 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm
Load Monitoring - Alarm | 0x0CF6 | 3319 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm
Load Monitoring - Alarm | 0x0D16 | 3351 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) – refer to register 3352 • Bit 0 = Validity of Overcurrent prealarm 90% alarm • Bit 1 = Validity of Overcurrent prealarm 105% alarm
Load Monitoring - Alarm | 0x0D17 | 3352 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) • Bit 0 = Status of Overcurrent prealarm 90% alarm • Bit 1 = Status of Overcurrent prealarm 105% alarm
Load Monitoring - Alarm | 0x0D1A | 3355 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the CALH1_AlmArray2 bitmap (0 = Invalid / 1 = Valid) – refer to register 3357 • Bit 0 = Validity of ERMS engaged Alarm (1) • Bit 1 = Validity of ERMS disengaged Alarm (1) (1) Applicable on product family in tab MasterPacT MTZ Active
Load Monitoring - Alarm | 0x0D1C | 3357 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) • Bit 0 = Status of ERMS engaged(1) • Bit 1 = Status of ERMS disengaged(1) (1) Applicable on product family in tab MasterPacT MTZ Active
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Configuration | 0x7925 | 31014 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the usage of the wireless device with: • 1 = Main/Incomer • 2 = Sub/Head of group • 3 = Heating • 4 = Cooling • 5 = HVAC • 6 = Ventilation • 7 = Lighting • 8 = Office Equipment • 9 = Cooking • 10 = Food refrigeration • 11 = Elevators • 12 = Computers • 13 = Renewable power source • 14 = Genset • 15 = Compressed air • 16 = Vapor • 17 = Machine • 18 = Process • 19 = Water • 20 = Other Sockets • 21 = Other • 22 = Electrical vehicle charging station • 23 = Loads associated with renewable power source • 24 = Plug loads • 25 = Air conditionning • 26 = Domestic hot water • 27 = Heating & air conditionning • 28 = Hot sanitary water • 29 = IT • 30 = Lighting (interior) • 31 = Lighting (exterior and park) • 32 = Mixed usages • 33 = Refrigeration • 34 = Special loads • 35 = Total • 36 = Transportation system • 37 = Water system pumps • 38 = Emergency lighting
Configuration | 0x7929 | 31018 | 1 | R | - | A | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Rated current of the protective device to the wireless device
Configuration | 0x792D | 31022 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the commodity of the wireless device 1. Electricity 2. Gas 3. Fuel oil 4. Air 5. Steam 6. Water 7. Environment 8. Other 9. Custom (Free text to enter): User can enter 10 custom values
Configuration | 0x792F | 31024 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Power supply type • 1 = Top • 2 = Bottom (default value)
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier : 16131 - LV933071W, LV933072W, LV933073W 16132 - LV947600W, LV947602W, LV947603W 17200 - A9MEM1520 17201 - A9MEM1521 17202 - A9MEM1522 17203 - A9MEM1540 17204 - A9MEM1541 17205 - A9MEM1542 17206 - A9MEM1560 17207 - A9MEM1561 17208 - A9MEM1562 17209 - A9MEM1563 17210 - A9MEM1570 17211 - A9MEM1571 17212 - A9MEM1572 17213 - A9MEM1543 17214 - A9MEM1573 17215 - A9MEM1564 17216 - A9MEM1574 17218 - A9MEM1575 17300 - EMS59440 17301 - EMS59443 17302 - A9XST114, ESST010B0400 17305 - SED-CO2-G-5045 17306 - SED-TRH-G-5045 17308 - PD100X001 17320 - SPTH150S 17321 - SPTH150M 17322 - SPTH200M 17350 - SMT10020 (V1) 17351 - SMT10020 (V2) 17660 - OVA44210, OVA44211, OVA44212, OVA44213, OVA44214, OVA44215, OVA47210, OVA47211, OVA47212, OVA47213, OVA47214, OVA47215, OVA59130, OVA59131, OVA59132, OVA59230, OVA59231, OVA59330, OVA59331, OV59430, OVA59431 17750 - LV429453 17751 - LV429454 17800 - LV434020 17801 - LV434021 17802 - LV434022 17803 - LV434023 17854 - PLTPPB1253P 17900 - A9XMC2D3 17901 - A9XMC1D3 17950 - PLTQO301P 17951 - PLTQO601P 17952 - PLTQO302P 17953 - PLTQO602P 17954 - PLTQO303P 17955 - PLTQO603P 17956 - PLTE601P 17957 - PLTE602P 17958 - PLTE603P 17969 - PLTR1203P 17970 - PLTR6003P 17971 - PLTR10003P 17972 - PLTR20003P 17973 - A9MEM1590 17974 - A9MEM1591 17975 - A9MEM1592 17976 - A9MEM1593 17980 - A9MEM1580 19500 - A9TYBE625, A9TYBE640 19501 - A9TAB1625, A9TAB1640, A9TAB2625, A9TAB2640 19502 - A9TDEC610, A9TDEC613, A9TDEC616, A9TDFC606, A9TDFC610, A9TDFC613, A9TDFC616, A9TDFC625, A9TDFC632, A9TDFC640, A9TDFD606, A9TDFD610, A9TDFD616, A9TDFD620, A9TDFD625, A9TDFD632 19503 - A9TPDD610, A9TPDD613, A9TPDD616, A9TPED610, A9TPED613, A9TPED616, A9TPED625, A9TPED632, A9TPED640 19504 - A9TYAE225, A9TYAE240, A9TYBE225, A9TYBE240 19505 - A9TAA1225, A9TAA1240, A9TAA225, A9TAA2240, A9TAB1225, A9TAB1240, A9TAB2225, A9TAB2240 19506 - A9TYAE625, A9TYAE640 19507 - A9TAA1625, A9TAA1640, A9TAA2625, A9TAA2640 19508 - A9TDND606, A9TDND610, A9TDND616, A9TDND620, A9TDND625, A9TDND632, A9TDNC606, A9TDNC610, A9TDNC616, A9TDNC625, A9TDNC632, A9TDNC640 19600 - A9V6E225, A9V6E240, A9V8E225, A9V8E240, A9Y6E625, A9Y6E640, A9Y8E625, A9Y8E640 20200 - ZBRT1 20201 - ZBRT2
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the device and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79AA | 31147 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Packet Error Rate (PER) of the device, received by Panel Server
Diagnostic Data | 0x79AC | 31149 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI of the device, received by Panel Server
Diagnostic Data | 0x79AE | 31151 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Link Quality Indicator (LQI) of the device, received by Panel Server
Diagnostic Data | 0x79AF | 31152 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER of gateway, calculated inside the Panel Server
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B4 | 31157 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER – Maximum value between device and Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server
Circuit breaker | 0x80E8 | 33001 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Circuit breaker position • 0 = Open • 1 = Close
Circuit breaker | 0x80E9 | 33002 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Circuit breaker trip indicator • 0 = Off • 1 = On
Circuit breaker | 0x80EA | 33003 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Circuit breaker trip electrical fault indicator • 0 = Off • 1 = On
Circuit breaker | 0x80EB | 33004 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Spring status indication • 0 = Breaker discharged • 1 = Breaker charged
Circuit breaker | 0x80EC | 33005 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Circuit breaker ready to close • 0 = Not Ready to Close • 1 = Ready to Close
Circuit breaker | 0x80ED | 33006 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Cirsuit breaker health status • 0 = not evaluated • 1 = ok • 2 = warning • 3 = malfunction
Circuit breaker | 0x80EE | 33007 | 2 | R | - | - | UINT32 |  | 0xFFFFFFFF | N | 3, 100-4 | Cumulated number of Trips
Circuit breaker | 0x80F0 | 33009 | 2 | R | - | - | UINT32 |  | 0xFFFFFFFF | N | 3, 100-4 | Cumulated number of Electrical Trips
Circuit breaker | 0x80F2 | 33011 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Phase A contact wear in %
Circuit breaker | 0x80F4 | 33013 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Phase B contact wear in %
Circuit breaker | 0x80F6 | 33015 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Phase C contact wear in %
Circuit breaker | 0x80F8 | 33017 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Neutral contact wear in %

## MasterPacT MTZ Active E
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Current Metering Data | 0x0BB7 | 3000 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A
Current Metering Data | 0x0BB9 | 3002 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B
Current Metering Data | 0x0BBB | 3004 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C
Current Metering Data | 0x0BBD | 3006 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral
Current Metering Data | 0x0BBF | 3008 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on ground or earth-leakage
Current Metering Data | 0x0BC1 | 3010 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of three phases RMS currents
Voltage Metering Data | 0x0BCB | 3020 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B
Voltage Metering Data | 0x0BCD | 3022 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C
Voltage Metering Data | 0x0BCF | 3024 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A
Voltage Metering Data | 0x0BD3 | 3028 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N
Voltage Metering Data | 0x0BD5 | 3030 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N
Voltage Metering Data | 0x0BD7 | 3032 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N
Power Metering Data | 0x0BED | 3054 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A
Power Metering Data | 0x0BEF | 3056 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B
Power Metering Data | 0x0BF1 | 3058 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C
Power Metering Data | 0x0BF3 | 3060 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power
Power Metering Data | 0x0BF5 | 3062 | 2 | R | - | VAR | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Reactive power on phase A
Power Metering Data | 0x0BF7 | 3064 | 2 | R | - | VAR | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Reactive power on phase B
Power Metering Data | 0x0BF9 | 3066 | 2 | R | - | VAR | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Reactive power on phase C
Power Metering Data | 0x0BFB | 3068 | 2 | R | - | VAR | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power
Power Metering Data | 0x0BFD | 3070 | 2 | R | - | VA | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Apparent power on phase A
Power Metering Data | 0x0BFF | 3072 | 2 | R | - | VA | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Apparent power on phase B
Power Metering Data | 0x0C01 | 3074 | 2 | R | - | VA | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Apparent power on phase C
Power Metering Data | 0x0C03 | 3076 | 2 | R | - | VA | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic)
Power Factor Metering Data | 0x0C05 | 3078 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Power factor on phase A
Power Factor Metering Data | 0x0C07 | 3080 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Power factor on phase B
Power Factor Metering Data | 0x0C09 | 3082 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Power factor on phase C
Power Factor Metering Data | 0x0C0B | 3084 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor
Power Factor Metering Data | 0x0C0D | 3086 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Power factor sign convention • 0 = IEC • 1 = IEEE
Frequency Metering Data | 0x0C25 | 3110 | 2 | R | - | Hz | Float32 |  | 0xFFC00000 | N | 3, 100-4 | AC frequency
Frequency Metering Data | 0x0C27 | 3112 | 2 | R | - | Hz | Float32 |  | 0xFFC00000 | N | 3, 100-4 | AC minimum frequency
Frequency Metering Data | 0x0C29 | 3114 | 2 | R | - | Hz | Float32 |  | 0xFFC00000 | N | 3, 100-4 | AC maximum frequency
Energy Data - Legacy Zone | 0x0CB7 | 3256 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial active energy delivered + received (resettable)
Energy Data - Legacy Zone | 0x0CBB | 3260 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial active energy counter. The value returns to zero by Panel Server.
Energy Data - Legacy Zone | 0x0CBF | 3264 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial active energy delivered (resettable)
Energy Data - Legacy Zone | 0x0CC3 | 3268 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial active energy delivered counter. The value returns to zero by Panel Server.
Energy Data - Legacy Zone | 0x0CC7 | 3272 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial active energy received (resettable)
Energy Data - Legacy Zone | 0x0CCB | 3276 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial active energy received counter. The value returns to zero by Panel Server.
Energy Data - Legacy Zone | 0x0CCF | 3280 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial reactive energy delivered (resettable)
Energy Data - Legacy Zone | 0x0CD3 | 3284 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial reactive energy delivered counter. The value returns to zero by Panel Server.
Energy Data - Legacy Zone | 0x0CD7 | 3288 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial reactive energy received (resettable)
Energy Data - Legacy Zone | 0x0CDB | 3292 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial reactive energy received counter. The value returns to zero by Panel Server.
Load Monitoring - Alarm | 0x0CE1 | 3298 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) – refer to register 3300 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 15 = Validity of Ground Fault Alarm (7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active
Load Monitoring - Alarm | 0x0CE3 | 3300 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 15 = Status of Ground Fault Alarm(7) • Bit 16–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag (7) Applicable on product family in tab MasterPacT MTZ Active
Load Monitoring - Alarm | 0x0CF5 | 3318 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) – refer to register 3319 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm
Load Monitoring - Alarm | 0x0CF6 | 3319 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm
Load Monitoring - Alarm | 0x0D14 | 3349 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) – refer to register 3350 • Bit 1 = Validity of OverVoltage protection 1P (59-1) alarm • Bit 2 = Validity of UnderVoltage protection 1P (27-1) alarm • Bit 3 = Validity of OverVoltage protection 3P (59-2) alarm • Bit 4 = Validity of UnderVoltage protection 3P (27-2) alarm
Load Monitoring - Alarm | 0x0D15 | 3350 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) • Bit 1 = Status of OverVoltage protection 1P (59-1) alarm • Bit 2 = Status of UnderVoltage protection 1P (27-1) alarm • Bit 3 = Status of OverVoltage protection 3P (59-2) alarm • Bit 4 = Status of UnderVoltage protection 3P (27-2) alarm
Load Monitoring - Alarm | 0x0D16 | 3351 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) – refer to register 3352 • Bit 0 = Validity of Overcurrent prealarm 90% alarm • Bit 1 = Validity of Overcurrent prealarm 105% alarm
Load Monitoring - Alarm | 0x0D17 | 3352 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) • Bit 0 = Status of Overcurrent prealarm 90% alarm • Bit 1 = Status of Overcurrent prealarm 105% alarm
Load Monitoring - Alarm | 0x0D1A | 3355 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the CALH1_AlmArray2 bitmap (0 = Invalid / 1 = Valid) – refer to register 3357 • Bit 0 = Validity of ERMS engaged Alarm (1) • Bit 1 = Validity of ERMS disengaged Alarm (1) (1) Applicable on product family in tab MasterPacT MTZ Active
Load Monitoring - Alarm | 0x0D1C | 3357 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) • Bit 0 = Status of ERMS engaged(1) • Bit 1 = Status of ERMS disengaged(1) (1) Applicable on product family in tab MasterPacT MTZ Active
Power Demand Data | 0x0EB5 | 3766 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Demand total active power
Power Demand Data | 0x0EB9 | 3770 | 2 | R | - | W | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Peak demand total active power
Power Demand Data | 0x0EBB | 3772 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Peak demand total active power timestamp
Current Demand Data | 0x0EC9 | 3786 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Current demand on phase A
Current Demand Data | 0x0ECB | 3788 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Current demand on phase B
Current Demand Data | 0x0ECD | 3790 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Current demand on phase C
Current Demand Data | 0x0ECF | 3792 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Current demand on neutral
Current Demand Data | 0x0ED1 | 3794 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Average of 3 phase current demands
Unbalance Data | 0x0F4E | 3919 | 2 | R | - | % | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Phase A current unbalance with respect to the average of 3 phase RMS currents
Unbalance Data | 0x0F50 | 3921 | 2 | R | - | % | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Phase B current unbalance with respect to the average of 3 phase RMS currents
Unbalance Data | 0x0F52 | 3923 | 2 | R | - | % | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Phase C current unbalance with respect to the average of 3 phase RMS currents
Unbalance Data | 0x0F54 | 3925 | 2 | R | - | % | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Maximum of 3 phase current unbalances
Unbalance Data | 0x0F56 | 3927 | 2 | R | - | % | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Maximum of maximum of 3 phase current unbalances
Unbalance Data | 0x0F58 | 3929 | 2 | R | - | % | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Phase-to-neutral A-N voltage unbalance with respect to the average of 3 phase-to-neutral RMS voltages
Unbalance Data | 0x0F5A | 3931 | 2 | R | - | % | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Phase-to-neutral B-N voltage unbalance with respect to the average of 3 phase-to-neutral RMS voltages
Unbalance Data | 0x0F5C | 3933 | 2 | R | - | % | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Phase-to-neutral C-N voltage unbalance with respect to the average of 3 phase-to-neutral RMS voltages
Unbalance Data | 0x0F5E | 3935 | 2 | R | - | % | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Maximum of 3 phase-to-neutral voltage unbalances
Unbalance Data | 0x0F60 | 3937 | 2 | R | - | % | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Maximum of maximum of 3 phase-to-neutral voltage unbalances (remark: stored with coincident average of 3 RMS phase-to-neutral voltages in V)
Unbalance Data | 0x0F62 | 3939 | 2 | R | - | % | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Phase-to-phase A-B voltage unbalance with respect to the average of 3 phase-to-phase RMS voltages
Unbalance Data | 0x0F64 | 3941 | 2 | R | - | % | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Phase-to-phase B-C voltage unbalance with respect to the average of 3 phase-to-phase RMS voltages
Unbalance Data | 0x0F66 | 3943 | 2 | R | - | % | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Phase-to-phase C-A voltage unbalance with respect to the average of 3 phase-to-phase RMS voltages
Unbalance Data | 0x0F68 | 3945 | 2 | R | - | % | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Maximum of 3 phase-to-phase voltage unbalances
Unbalance Data | 0x0F6A | 3947 | 2 | R | - | % | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Maximum of maximum of 3 phase-to-phase voltage unbalances (remark: stored with coincident average of 3 RMS phase-to-phase voltages in V)
Energy Data – New Zone | 0x1390 | 5009 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy delivered (resettable)
Energy Data – New Zone | 0x1398 | 5017 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy received (resettable)
Energy Data – New Zone | 0x13B8 | 5049 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase A delivered (resettable)
Energy Data – New Zone | 0x13C0 | 5057 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase A received (resettable)
Energy Data – New Zone | 0x13E0 | 5089 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase B delivered (resettable)
Energy Data – New Zone | 0x13E8 | 5097 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase B received (resettable)
Energy Data – New Zone | 0x1408 | 5129 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase C delivered (resettable)
Energy Data – New Zone | 0x1410 | 5137 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase C received (resettable)
Energy Data – New Zone | 0x1438 | 5177 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy delivered (resettable)
Energy Data – New Zone | 0x1448 | 5193 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy received (resettable)
Energy Data – New Zone | 0x1470 | 5233 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy on phase A delivered (resettable)
Energy Data – New Zone | 0x1478 | 5241 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy on phase A received (resettable)
Energy Data – New Zone | 0x1498 | 5273 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy on phase B delivered (resettable)
Energy Data – New Zone | 0x14A0 | 5281 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy on phase B received (resettable)
Energy Data – New Zone | 0x14C0 | 5313 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy on phase C delivered (resettable)
Energy Data – New Zone | 0x14C8 | 5321 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy on phase C received (resettable)
Energy Data – New Zone | 0x14F4 | 5365 | 4 | R | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Apparent energy delivered + received (resettable)
Energy Data – New Zone | 0x150C | 5389 | 4 | R | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Apparent energy on phase A (resettable)
Energy Data – New Zone | 0x1534 | 5429 | 4 | R | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Apparent energy on phase B (resettable)
Energy Data – New Zone | 0x155C | 5469 | 4 | R | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Apparent energy on phase C (resettable)
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Configuration | 0x7925 | 31014 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the usage of the wireless device with: • 1 = Main/Incomer • 2 = Sub/Head of group • 3 = Heating • 4 = Cooling • 5 = HVAC • 6 = Ventilation • 7 = Lighting • 8 = Office Equipment • 9 = Cooking • 10 = Food refrigeration • 11 = Elevators • 12 = Computers • 13 = Renewable power source • 14 = Genset • 15 = Compressed air • 16 = Vapor • 17 = Machine • 18 = Process • 19 = Water • 20 = Other Sockets • 21 = Other • 22 = Electrical vehicle charging station • 23 = Loads associated with renewable power source • 24 = Plug loads • 25 = Air conditionning • 26 = Domestic hot water • 27 = Heating & air conditionning • 28 = Hot sanitary water • 29 = IT • 30 = Lighting (interior) • 31 = Lighting (exterior and park) • 32 = Mixed usages • 33 = Refrigeration • 34 = Special loads • 35 = Total • 36 = Transportation system • 37 = Water system pumps • 38 = Emergency lighting
Configuration | 0x7929 | 31018 | 1 | R | - | A | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Rated current of the protective device to the wireless device
Configuration | 0x792A | 31019 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Electrical network system type • 0 = Unknown system type • 3 = 3PH3W • 11= 3PH4W
Configuration | 0x792B | 31020 | 2 | R | - | V | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Rated voltage: • LN rated voltage for single phase wiring systems • LL rated voltage for 3 phases wiring systems
Configuration | 0x792D | 31022 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the commodity of the wireless device 1. Electricity 2. Gas 3. Fuel oil 4. Air 5. Steam 6. Water 7. Environment 8. Other 9. Custom (Free text to enter): User can enter 10 custom values
Configuration | 0x792E | 31023 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Reset the Peak Active Power Demand for this wireless device, Any value writen will reset Peak Active Power Demand to 0
Configuration | 0x792F | 31024 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Power supply type • 1 = Top • 2 = Bottom (default value)
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier : 16131 - LV933071W, LV933072W, LV933073W 16132 - LV947600W, LV947602W, LV947603W 17200 - A9MEM1520 17201 - A9MEM1521 17202 - A9MEM1522 17203 - A9MEM1540 17204 - A9MEM1541 17205 - A9MEM1542 17206 - A9MEM1560 17207 - A9MEM1561 17208 - A9MEM1562 17209 - A9MEM1563 17210 - A9MEM1570 17211 - A9MEM1571 17212 - A9MEM1572 17213 - A9MEM1543 17214 - A9MEM1573 17215 - A9MEM1564 17216 - A9MEM1574 17218 - A9MEM1575 17300 - EMS59440 17301 - EMS59443 17302 - A9XST114, ESST010B0400 17305 - SED-CO2-G-5045 17306 - SED-TRH-G-5045 17308 - PD100X001 17320 - SPTH150S 17321 - SPTH150M 17322 - SPTH200M 17350 - SMT10020 (V1) 17351 - SMT10020 (V2) 17660 - OVA44210, OVA44211, OVA44212, OVA44213, OVA44214, OVA44215, OVA47210, OVA47211, OVA47212, OVA47213, OVA47214, OVA47215, OVA59130, OVA59131, OVA59132, OVA59230, OVA59231, OVA59330, OVA59331, OV59430, OVA59431 17750 - LV429453 17751 - LV429454 17800 - LV434020 17801 - LV434021 17802 - LV434022 17803 - LV434023 17854 - PLTPPB1253P 17900 - A9XMC2D3 17901 - A9XMC1D3 17950 - PLTQO301P 17951 - PLTQO601P 17952 - PLTQO302P 17953 - PLTQO602P 17954 - PLTQO303P 17955 - PLTQO603P 17956 - PLTE601P 17957 - PLTE602P 17958 - PLTE603P 17969 - PLTR1203P 17970 - PLTR6003P 17971 - PLTR10003P 17972 - PLTR20003P 17973 - A9MEM1590 17974 - A9MEM1591 17975 - A9MEM1592 17976 - A9MEM1593 17980 - A9MEM1580 19500 - A9TYBE625, A9TYBE640 19501 - A9TAB1625, A9TAB1640, A9TAB2625, A9TAB2640 19502 - A9TDEC610, A9TDEC613, A9TDEC616, A9TDFC606, A9TDFC610, A9TDFC613, A9TDFC616, A9TDFC625, A9TDFC632, A9TDFC640, A9TDFD606, A9TDFD610, A9TDFD616, A9TDFD620, A9TDFD625, A9TDFD632 19503 - A9TPDD610, A9TPDD613, A9TPDD616, A9TPED610, A9TPED613, A9TPED616, A9TPED625, A9TPED632, A9TPED640 19504 - A9TYAE225, A9TYAE240, A9TYBE225, A9TYBE240 19505 - A9TAA1225, A9TAA1240, A9TAA225, A9TAA2240, A9TAB1225, A9TAB1240, A9TAB2225, A9TAB2240 19506 - A9TYAE625, A9TYAE640 19507 - A9TAA1625, A9TAA1640, A9TAA2625, A9TAA2640 19508 - A9TDND606, A9TDND610, A9TDND616, A9TDND620, A9TDND625, A9TDND632, A9TDNC606, A9TDNC610, A9TDNC616, A9TDNC625, A9TDNC632, A9TDNC640 19600 - A9V6E225, A9V6E240, A9V8E225, A9V8E240, A9Y6E625, A9Y6E640, A9Y8E625, A9Y8E640 20200 - ZBRT1 20201 - ZBRT2
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the device and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79AA | 31147 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Packet Error Rate (PER) of the device, received by Panel Server
Diagnostic Data | 0x79AC | 31149 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI of the device, received by Panel Server
Diagnostic Data | 0x79AE | 31151 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Link Quality Indicator (LQI) of the device, received by Panel Server
Diagnostic Data | 0x79AF | 31152 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER of gateway, calculated inside the Panel Server
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B4 | 31157 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER – Maximum value between device and Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server
Circuit breaker | 0x80E8 | 33001 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Circuit breaker position • 0 = Open • 1 = Close
Circuit breaker | 0x80E9 | 33002 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Circuit breaker trip indicator • 0 = Off • 1 = On
Circuit breaker | 0x80EA | 33003 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Circuit breaker trip electrical fault indicator • 0 = Off • 1 = On
Circuit breaker | 0x80EB | 33004 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Spring status indication • 0 = Breaker discharged • 1 = Breaker charged
Circuit breaker | 0x80EC | 33005 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Circuit breaker ready to close • 0 = Not Ready to Close • 1 = Ready to Close
Circuit breaker | 0x80ED | 33006 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Cirsuit breaker health status • 0 = not evaluated • 1 = ok • 2 = warning • 3 = malfunction
Circuit breaker | 0x80EE | 33007 | 2 | R | - | - | UINT32 |  | 0xFFFFFFFF | N | 3, 100-4 | Cumulated number of Trips
Circuit breaker | 0x80F0 | 33009 | 2 | R | - | - | UINT32 |  | 0xFFFFFFFF | N | 3, 100-4 | Cumulated number of Electrical Trips
Circuit breaker | 0x80F2 | 33011 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Phase A contact wear in %
Circuit breaker | 0x80F4 | 33013 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Phase B contact wear in %
Circuit breaker | 0x80F6 | 33015 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Phase C contact wear in %
Circuit breaker | 0x80F8 | 33017 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Neutral contact wear in %

## ExiwayLight
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Configuration | 0x7925 | 31014 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the usage of the wireless device with: • 1 = Main/Incomer • 2 = Sub/Head of group • 3 = Heating • 4 = Cooling • 5 = HVAC • 6 = Ventilation • 7 = Lighting • 8 = Office Equipment • 9 = Cooking • 10 = Food refrigeration • 11 = Elevators • 12 = Computers • 13 = Renewable power source • 14 = Genset • 15 = Compressed air • 16 = Vapor • 17 = Machine • 18 = Process • 19 = Water • 20 = Other Sockets • 21 = Other • 22 = Electrical vehicle charging station • 23 = Loads associated with renewable power source • 24 = Plug loads • 25 = Air conditionning • 26 = Domestic hot water • 27 = Heating & air conditionning • 28 = Hot sanitary water • 29 = IT • 30 = Lighting (interior) • 31 = Lighting (exterior and park) • 32 = Mixed usages • 33 = Refrigeration • 34 = Special loads • 35 = Total • 36 = Transportation system • 37 = Water system pumps • 38 = Emergency lighting
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier : 16131 - LV933071W, LV933072W, LV933073W 16132 - LV947600W, LV947602W, LV947603W 17200 - A9MEM1520 17201 - A9MEM1521 17202 - A9MEM1522 17203 - A9MEM1540 17204 - A9MEM1541 17205 - A9MEM1542 17206 - A9MEM1560 17207 - A9MEM1561 17208 - A9MEM1562 17209 - A9MEM1563 17210 - A9MEM1570 17211 - A9MEM1571 17212 - A9MEM1572 17213 - A9MEM1543 17214 - A9MEM1573 17215 - A9MEM1564 17216 - A9MEM1574 17218 - A9MEM1575 17300 - EMS59440 17301 - EMS59443 17302 - A9XST114, ESST010B0400 17305 - SED-CO2-G-5045 17306 - SED-TRH-G-5045 17308 - PD100X001 17320 - SPTH150S 17321 - SPTH150M 17322 - SPTH200M 17350 - SMT10020 (V1) 17351 - SMT10020 (V2) 17660 - OVA44210, OVA44211, OVA44212, OVA44213, OVA44214, OVA44215, OVA47210, OVA47211, OVA47212, OVA47213, OVA47214, OVA47215, OVA59130, OVA59131, OVA59132, OVA59230, OVA59231, OVA59330, OVA59331, OV59430, OVA59431 17750 - LV429453 17751 - LV429454 17800 - LV434020 17801 - LV434021 17802 - LV434022 17803 - LV434023 17854 - PLTPPB1253P 17900 - A9XMC2D3 17901 - A9XMC1D3 17950 - PLTQO301P 17951 - PLTQO601P 17952 - PLTQO302P 17953 - PLTQO602P 17954 - PLTQO303P 17955 - PLTQO603P 17956 - PLTE601P 17957 - PLTE602P 17958 - PLTE603P 17969 - PLTR1203P 17970 - PLTR6003P 17971 - PLTR10003P 17972 - PLTR20003P 17973 - A9MEM1590 17974 - A9MEM1591 17975 - A9MEM1592 17976 - A9MEM1593 17980 - A9MEM1580 19500 - A9TYBE625, A9TYBE640 19501 - A9TAB1625, A9TAB1640, A9TAB2625, A9TAB2640 19502 - A9TDEC610, A9TDEC613, A9TDEC616, A9TDFC606, A9TDFC610, A9TDFC613, A9TDFC616, A9TDFC625, A9TDFC632, A9TDFC640, A9TDFD606, A9TDFD610, A9TDFD616, A9TDFD620, A9TDFD625, A9TDFD632 19503 - A9TPDD610, A9TPDD613, A9TPDD616, A9TPED610, A9TPED613, A9TPED616, A9TPED625, A9TPED632, A9TPED640 19504 - A9TYAE225, A9TYAE240, A9TYBE225, A9TYBE240 19505 - A9TAA1225, A9TAA1240, A9TAA225, A9TAA2240, A9TAB1225, A9TAB1240, A9TAB2225, A9TAB2240 19506 - A9TYAE625, A9TYAE640 19507 - A9TAA1625, A9TAA1640, A9TAA2625, A9TAA2640 19508 - A9TDND606, A9TDND610, A9TDND616, A9TDND620, A9TDND625, A9TDND632, A9TDNC606, A9TDNC610, A9TDNC616, A9TDNC625, A9TDNC632, A9TDNC640 19600 - A9V6E225, A9V6E240, A9V8E225, A9V8E240, A9Y6E625, A9Y6E640, A9Y8E625, A9Y8E640 20200 - ZBRT1 20201 - ZBRT2
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the device and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79AC | 31149 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI of the device, received by Panel Server
Diagnostic Data | 0x79AE | 31151 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Link Quality Indicator (LQI) of the device, received by Panel Server
Diagnostic Data | 0x79AF | 31152 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER of gateway, calculated inside the Panel Server
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B4 | 31157 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER – Maximum value between device and Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server
Diagnostic Data | 0x9A34 | 39477 | 2 | R | - | SEC | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Duration in seconds since last duration test
Diagnostic Data | 0x9A36 | 39479 | 2 | R | - | SEC | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Duration in seconds since last functional test
Diagnostic Data | 0x9A38 | 39481 | 2 | R | - | SEC | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Duration in seconds until next duration test
Diagnostic Data | 0x9A3A | 39483 | 2 | R | - | SEC | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Duration in seconds until next functional test
Diagnostic Data | 0x9A3C | 39485 | 2 | R | - | - | UINT32 |  | 0xFFFFFFFF | Y | 3, 100-4 | Number of emergency
Diagnostic Data | 0x9A3E | 39487 | 2 | R | - | SEC | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Emergency mode duration in seconds
Status | 0x9A4B | 39500 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the light status ENUM { MP_LIGHT_INIT = 0, //Initialization MP_LIGHT_OFF = 1, //led is off MP_LIGHT_PERMANENT = 2, //led is on MP_LIGHT_FIRE_ALARM = 3 , // indication of fire MP_LIGHT_LINE_TEST = 4 , // led is performing identification 0x05 -> 0xFF = Reserved } Important: light status is only applicable when it is not in emergency mode (register will be invalid due to the addition of a quality except)
Status | 0x9A4C | 39501 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Emergency luminaire status/Luminaire state array quality (0 = Invalid / 1= Valid) - refer to register 39503
Status | 0x9A4D | 39502 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Emergency luminaire status/Luminaire state array quality (0 = Invalid / 1= Valid) - refer to register 39504
Status | 0x9A4E | 39503 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Emergency luminaire status/Luminaire state array quality - bitmap status • Bit 0 = Emergency mode • Bit 3 = Inhibit Test • Bit 4 = Installation Error • Bit 5 = Battery Disconnected • Bit 8 = Serial communication error • Bit 15 = Functional Test failed
Status | 0x9A4F | 39504 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Emergency luminaire status/Luminaire state array quality - bitmap status • Bit 1 = Functional Test Postponed • Bit 3 = Functional Test Ongoing • Bit 8 = Duration Test failed • Bit 10 = Duration Test Postponed • Bit 12 = Duration Test Ongoing
Control | 0x9A50 | 39505 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Switch on / switch off the light (WARNING: DO NOT WORK ON DEVICE FOR THE FRENCH MARKET) ENUM { Off = 0, On = 1, } For feedback information (status), refer to register 39500
Control | 0x9A51 | 39506 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Enable or disable the tests (functionnal & duration tests): ENUM { Enable = 0, Disable = 1, } For feedback information (status), refer to register 39503 and check the following bits in the bitmap: • Bit 3 (Inhibit Test) // 0 = Enabled, 1 = Disabled
Control | 0x9A52 | 39507 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | Start a manual functional test (in addition to the periodical functional autotests): ENUM { Start = 1, } For feedback information (test result status), refer to register 39503 and check the following bits in the bitmap: • Bit 15 (Functional Test failed) // 1=Test failed • Bit 17 (Functional Test Postponed) // 1= Test postponed • Bit 19 (Functional Test Ongoing) // 1=Test ongoing

## ZBRT
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier : 16131 - LV933071W, LV933072W, LV933073W 16132 - LV947600W, LV947602W, LV947603W 17200 - A9MEM1520 17201 - A9MEM1521 17202 - A9MEM1522 17203 - A9MEM1540 17204 - A9MEM1541 17205 - A9MEM1542 17206 - A9MEM1560 17207 - A9MEM1561 17208 - A9MEM1562 17209 - A9MEM1563 17210 - A9MEM1570 17211 - A9MEM1571 17212 - A9MEM1572 17213 - A9MEM1543 17214 - A9MEM1573 17215 - A9MEM1564 17216 - A9MEM1574 17218 - A9MEM1575 17300 - EMS59440 17301 - EMS59443 17302 - A9XST114, ESST010B0400 17305 - SED-CO2-G-5045 17306 - SED-TRH-G-5045 17308 - PD100X001 17320 - SPTH150S 17321 - SPTH150M 17322 - SPTH200M 17350 - SMT10020 (V1) 17351 - SMT10020 (V2) 17660 - OVA44210, OVA44211, OVA44212, OVA44213, OVA44214, OVA44215, OVA47210, OVA47211, OVA47212, OVA47213, OVA47214, OVA47215, OVA59130, OVA59131, OVA59132, OVA59230, OVA59231, OVA59330, OVA59331, OV59430, OVA59431 17750 - LV429453 17751 - LV429454 17800 - LV434020 17801 - LV434021 17802 - LV434022 17803 - LV434023 17854 - PLTPPB1253P 17900 - A9XMC2D3 17901 - A9XMC1D3 17950 - PLTQO301P 17951 - PLTQO601P 17952 - PLTQO302P 17953 - PLTQO602P 17954 - PLTQO303P 17955 - PLTQO603P 17956 - PLTE601P 17957 - PLTE602P 17958 - PLTE603P 17969 - PLTR1203P 17970 - PLTR6003P 17971 - PLTR10003P 17972 - PLTR20003P 17973 - A9MEM1590 17974 - A9MEM1591 17975 - A9MEM1592 17976 - A9MEM1593 17980 - A9MEM1580 19500 - A9TYBE625, A9TYBE640 19501 - A9TAB1625, A9TAB1640, A9TAB2625, A9TAB2640 19502 - A9TDEC610, A9TDEC613, A9TDEC616, A9TDFC606, A9TDFC610, A9TDFC613, A9TDFC616, A9TDFC625, A9TDFC632, A9TDFC640, A9TDFD606, A9TDFD610, A9TDFD616, A9TDFD620, A9TDFD625, A9TDFD632 19503 - A9TPDD610, A9TPDD613, A9TPDD616, A9TPED610, A9TPED613, A9TPED616, A9TPED625, A9TPED632, A9TPED640 19504 - A9TYAE225, A9TYAE240, A9TYBE225, A9TYBE240 19505 - A9TAA1225, A9TAA1240, A9TAA225, A9TAA2240, A9TAB1225, A9TAB1240, A9TAB2225, A9TAB2240 19506 - A9TYAE625, A9TYAE640 19507 - A9TAA1625, A9TAA1640, A9TAA2625, A9TAA2640 19508 - A9TDND606, A9TDND610, A9TDND616, A9TDND620, A9TDND625, A9TDND632, A9TDNC606, A9TDNC610, A9TDNC616, A9TDNC625, A9TDNC632, A9TDNC640 19600 - A9V6E225, A9V6E240, A9V8E225, A9V8E240, A9Y6E625, A9Y6E640, A9Y8E625, A9Y8E640 20200 - ZBRT1 20201 - ZBRT2
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between the device and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server
Digital input | 0x84FA | 34043 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Timestamp of last change of Digital Input 1 status
Digital input | 0x8510 | 34065 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the logical status of the Digital Input 1 (takes into account the configured polarity) ENUM { ON = 1, //Active OFF = 0, //Inactive Undetermined = 65535 //Invalid value }