## EM4200 Device
Device Object | Property | R/W | NV | Value | Additional Information
| Object _Identifier |  |  | Pseudo-Random
| Object_Name | R/W | NV | Schneider Electric EM42xx Energy Meter SN | Writable up to 127 Bytes
| Object_Type | R |  | Device (8)
| System_Status | R |  | Operational (0)
| Vendor_Name | R | NV | Schneider Electric
| Vendor_Identifier | R | NV | 335
| Model_Name | R | NV | EM42xx Energy Meter
| Firmware_Revision | R |  | OS Version 1.00.20
| Application_Software_Version | R |  | RS Version 1.00.07
| Location | R/W | NV | Location | Writable up to 127 Bytes
| Description | R | NV | Schneider Electric EM42xx Energy Meter SN
| Protocol_Version | R |  | 1
| Protocol_Revision | R |  | 12
| Protocol_Services_Supported | R |  | BACnet Services Supported
| Protocol_Object_Types_Supported | R |  | BACnet Object Types Supported
| Object_List | R |  | Array of BACnet Object Identifiers
| Max_APDU_Length_Accepted | R |  | 480
| Segmentation_Supported | R | NV | Segmentation Not Supported
| Local_Time | R |  | Time
| Local_Date | R |  | Date
| UTC_Offset | R | NV | Offset
| Daylight_Savings_Status | R | NV | Boolean
| APDU_Timeout | R | NV | 3000
| Number_Of_APDU_Retries | R | NV | 3
| Max_Master | R/W | NV | 127 | Writable 1 - 127
| Max_Info_Frames | R | NV | 1
| Device_Address_Binding | R | NV | {}
| Database_Revision | R | NV | Revision
| Active_COV_Subscriptions | R | NV | List of BACnet COV Subscriptions

## Analog Inputs
Analog Inputs | AI # | Object Name | BACnet Description | RW | NV | Units | Range | Default COV Increment | Additional Information
UniDirectional Summary
| 1 | kWh | Real (Active, P) Energy Consumption | R | NV | kWh |  | 1
| 2 | kVARh | Reactive (Q) Energy Consumption | R | NV | kVARh |  | 1
| 3 | kVAh | Apparent (S) Energy Consumption | R | NV | kVAh |  | 1
| 4 | kW_Total | Total Real (Active, P) Power | R |  | KW |  | 1
| 5 | kVAR_Total | Total Reactive (Q) Power | R |  | kVAR |  | 1
| 6 | kVA_Total | Total Apparent (S) Power | R |  | kVA |  | 1
| 7 | PF_Avg | Average Power Factor (P/S) | R |  |  | 0.00 - 1.00 | 0.1
| 8 | Voltage_LL_Avg | Voltage Line to Line (U): Average of Active Phases | R |  | Volts |  | 1
| 9 | Voltage_LN_Avg | Voltage Line to Neutral (V): Average of Active Phases | R |  | Volts |  | 1
| 10 | Current_Avg | Current (I): Average of Active Phases | R |  | Amps |  | 5
| 11 | Frequency | Frequency Hz | R |  | Hz | 45.0 - 65.0 | 0.5
| 12 | kW_Present_Demand | Total Real (Active, P) Power Present Demand | R |  | kW |  | 0
| 13 | kVAR_Present_Demand | Total Reactive (Q) Power Present Demand | R |  | kVAR |  | 0
| 14 | kVA_Present_Demand | Total Apparent (S) Power Present Demand | R |  | kVA |  | 0
| 15 | kW_Max_Demand | Total Real (Active, P) Power Max Demand | R | NV | kW |  | 0
| 16 | kVAR_Max_Demand | Total Reactive (Q) Power Max Demand | R | NV | kVAR |  | 0
| 17 | kVA_Max_Demand | Total Apparent (S) Power Max Demand | R | NV | kVA |  | 0
UniDirectional Per Phase
| 18 | kWh_L1 | Real (Active, P) Energy Consumption L1 | R | NV | kWh |  | 1
| 19 | kWh_L2 | Real (Active, P) Energy Consumption L2 | R | NV | kWh |  | 1
| 20 | kWh_L3 | Real (Active, P) Energy Consumption L3 | R | NV | kWh |  | 1
| 21 | kVARh_L1 | Reactive (Q) Energy Consumption L1 | R | NV | kVARh |  | 1
| 22 | kVARh_L2 | Reactive (Q) Energy Consumption L2 | R | NV | kVARh |  | 1
| 23 | kVARh_L3 | Reactive (Q) Energy Consumption L3 | R | NV | kVARh |  | 1
| 24 | kVAh_L1 | Apparent (S) Energy Consumption L1 | R | NV | kVAh |  | 1
| 25 | kVAh_L2 | Apparent (S) Energy Consumption L2 | R | NV | kVAh |  | 1
| 26 | kVAh_L3 | Apparent (S) Energy Consumption L3 | R | NV | kVAh |  | 1
| 27 | kW_L1 | Real (Active, P) Power L1 | R |  | kW |  | 1
| 28 | kW_L2 | Real (Active, P) Power L2 | R |  | kW |  | 1
| 29 | kW_L3 | Real (Active, P) Power L3 | R |  | kW |  | 1
| 30 | kVAR_L1 | Reactive (Q) Power L1 | R |  | kVAR |  | 1
| 31 | kVAR_L2 | Reactive (Q) Power L2 | R |  | kVAR |  | 1
| 32 | kVAR_L3 | Reactive (Q) Power L3 | R |  | kVAR |  | 1
| 33 | kVA_L1 | Apparent (S) Power L1 | R |  | kVA |  | 1
| 34 | kVA_L2 | Apparent (S) Power L2 | R |  | kVA |  | 1
| 35 | kVA_L3 | Apparent (S) Power L3 | R |  | kVA |  | 1
| 36 | PF_L1 | Power Factor L1 | R |  |  | 0.00 - 1.00 | 0.1
| 37 | PF_L2 | Power Factor L2 | R |  |  | 0.00 - 1.00 | 0.1
| 38 | PF_L3 | Power Factor L3 | R |  |  | 0.00 - 1.00 | 0.1
| 39 | Voltage_L12 | Voltage L1-L2 (U12) | R |  | Volts |  | 1
| 40 | Voltage_L23 | Voltage L2-L3 (U23) | R |  | Volts |  | 1
| 41 | Voltage_L31 | Voltage L3-L1 (U31) | R |  | Volts |  | 1
| 42 | Voltage_L1 | Voltage L1-N (V1) | R |  | Volts |  | 1
| 43 | Voltage_L2 | Voltage L2-N (V2) | R |  | Volts |  | 1
| 44 | Voltage_L3 | Voltage L3-N (V3) | R |  | Volts |  | 1
| 45 | Current_L1 | Current L1 (I1) | R |  | Amps |  | 5
| 46 | Current_L2 | Current L2 (I2) | R |  | Amps |  | 5
| 47 | Current_L3 | Current L3 (I3) | R |  | Amps |  | 5
| 48 | Current_N | Current Neutral (IN) | R |  | Amps |  | 5
BiDirectional Summary
| 49 | kWh Net | Real (Active, P) Energy Consumption: Net (Import - Export) | R | NV | kWh |  | 1
| 50 | kWh_Import | Real (Active, P) Energy Consumption: Import | R | NV | kWh |  | 1
| 51 | kWh_Export | Real (Active, P) Energy Consumption: Export | R | NV | kWh |  | 1
| 52 | kVARh_Q1 | Reactive (Q) Energy Consumption: Quadrant 1 | R | NV | kVARh |  | 1
| 53 | kVARh_Q2 | Reactive (Q) Energy Consumption: Quadrant 2 | R | NV | kVARh |  | 1
| 54 | kVARh_Q3 | Reactive (Q) Energy Consumption: Quadrant 3 | R | NV | kVARh |  | 1
| 55 | kVARh_Q4 | Reactive (Q) Energy Consumption: Quadrant 4 | R | NV | kVARh |  | 1
| 56 | kVAh_Net | Apparent (S) Energy Comsumption: Net (Import - Export) | R | NV | kVAh |  | 1
| 57 | kVAh_Import | Apparent (S) Energy Consumption: Import | R | NV | kVAh |  | 1
| 58 | kVAh_Export | Apparent (S) Energy Consumption: Export | R | NV | kVAh |  | 1
| 59 | Bi-Dir_kW_Total | Bi-Directional Total Real (Active ,P) Power | R |  | kW |  | 1
| 60 | Bi-Dir_kVAR_Total | Bi-Directional Total Reactive (Q) Power | R |  | kVAR |  | 1
| 61 | Bi-Dir_PF_Avg | Bi-Directional Average Power Factor | R |  |  | -1.00 - 1.00 | 0.1
| 62 | Bi-Dir_kW_Present_Demand | Bi-Directional Total Real (Active ,P) Power Present Demand | R |  | kW |  | 0
| 63 | Bi-Dir_kVAR_Present_Demand | Bi-Directional Total Reactive (Q) Power Present Demand | R |  | kVAR |  | 0
| 64 | Bi-Dir_kVA_Present Demand | Bi-Directional Total Apparent (S) Power Present Demand | R |  | kVA |  | 0
| 65 | kW_Max_Demand_Import | Total Real (Active ,P) Power Max Demand: Import | R | NV | kW |  | 0
| 66 | kVAR_Max_Demand_Import | Total Reactive (Q) Power Max Demand: Import | R | NV | kVAR |  | 0
| 67 | kVA_Max_Demand_Import | Total Apparent (S) Power Max Demand: Import | R | NV | kVA |  | 0
| 68 | kW_Max_Demand_Export | Total Real (Active ,P) Power Max Demand: Export | R | NV | kW |  | 0
| 69 | kVAR_Max_Demand_Export | Total Reactive (Q) Power Max Demand: Export | R | NV | kVAR |  | 0
| 70 | kVA_Max_Demand_Export | Total Apparent (S) Power Max Demand: Export | R | NV | kVA |  | 0
BiDirectional Per Phase
| 71 | kWh_Import_L1 | Real (Active, P) Energy Consumption: Import L1 | R | NV | kWh |  | 1
| 72 | kWh_Import_L2 | Real (Active, P) Energy Consumption: Import L2 | R | NV | kWh |  | 1
| 73 | kWh_Import_L3 | Real (Active, P) Energy Consumption: Import L3 | R | NV | kWh |  | 1
| 74 | kWh_Export_L1 | Real (Active, P) Energy Consumption: Export L1 | R | NV | kWh |  | 1
| 75 | kWh_Export_L2 | Real (Active, P) Energy Consumption: Export L2 | R | NV | kWh |  | 1
| 76 | kWh_Export_L3 | Real (Active, P) Energy Consumption: Export L3 | R | NV | kWh |  | 1
| 77 | kVARh_Q1_L1 | Reactive (Q) Energy Consumption: Quadrant 1 L1 | R | NV | kVARh |  | 1
| 78 | kVARh_Q1_L2 | Reactive (Q) Energy Consumption: Quadrant 1 L2 | R | NV | kVARh |  | 1
| 79 | kVARh_Q1_L3 | Reactive (Q) Energy Consumption: Quadrant 1 L3 | R | NV | kVARh |  | 1
| 80 | kVARh_Q2_L1 | Reactive (Q) Energy Consumption: Quadrant 2 L1 | R | NV | kVARh |  | 1
| 81 | kVARh_Q2_L2 | Reactive (Q) Energy Consumption: Quadrant 2 L2 | R | NV | kVARh |  | 1
| 82 | kVARh_Q2_L3 | Reactive (Q) Energy Consumption: Quadrant 2 L3 | R | NV | kVARh |  | 1
| 83 | kVARh_Q3_L1 | Reactive (Q) Energy Consumption: Quadrant 3 L1 | R | NV | kVARh |  | 1
| 84 | kVARh_Q3_L2 | Reactive (Q) Energy Consumption: Quadrant 3 L2 | R | NV | kVARh |  | 1
| 85 | kVARh_Q3_L3 | Reactive (Q) Energy Consumption: Quadrant 3 L3 | R | NV | kVARh |  | 1
| 86 | kVARh_Q4_L1 | Reactive (Q) Energy Consumption: Quadrant 4 L1 | R | NV | kVARh |  | 1
| 87 | kVARh_Q4_L2 | Reactive (Q) Energy Consumption: Quadrant 4 L2 | R | NV | kVARh |  | 1
| 88 | kVARh_Q4_L3 | Reactive (Q) Energy Consumption: Quadrant 4 L3 | R | NV | kVARh |  | 1
| 89 | kVAh_Import_L1 | Apparent (S) Energy Consumption: ImportL1 | R | NV | kVAh |  | 1
| 90 | kVAh_Import_L2 | Apparent (S) Energy Consumption: ImportL2 | R | NV | kVAh |  | 1
| 91 | kVAh_Import_L3 | Apparent (S) Energy Consumption: ImportL3 | R | NV | kVAh |  | 1
| 92 | kVAh_Export_L1 | Apparent (S) Energy Consumption: ExportL1 | R | NV | kVAh |  | 1
| 93 | kVAh_Export_L2 | Apparent (S) Energy Consumption: ExportL2 | R | NV | kVAh |  | 1
| 94 | kVAh_Export_L3 | Apparent (S) Energy Consumption: ExportL3 | R | NV | kVAh |  | 1
| 95 | Bi-Dir_kW_L1 | Bi-Directional Real (Active, P) Power L1 | R |  | kW |  | 1
| 96 | Bi-Dir_kW_L2 | Bi-Directional Real (Active, P) Power L2 | R |  | kW |  | 1
| 97 | Bi-Dir_kW_L3 | Bi-Directional Real (Active, P) Power L3 | R |  | kW |  | 1
| 98 | Bi-Dir_kVAR_L1 | Bi-Directional Reactive (Q) Power L1 | R |  | kVAR |  | 1
| 99 | Bi-Dir_kVAR_L2 | Bi-Directional Reactive (Q) Power L2 | R |  | kVAR |  | 1
| 100 | Bi-Dir_kVAR_L3 | Bi-Directional Reactive (Q) Power L3 | R |  | kVAR |  | 1
| 101 | Bi-Dir_PF_L1 | Bi-Directional Power Factor L1 | R |  |  | -1.00 - 1.00 | 0.1
| 102 | Bi-Dir_PF_L2 | Bi-Directional Power Factor L2 | R |  |  | -1.00 - 1.00 | 0.1
| 103 | Bi-Dir_PF_L3 | Bi-Directional Power Factor L3 | R |  |  | -1.00 - 1.00 | 0.1

## Analog Values
Analog Values | AV# | Object Name | BACnet Description | RW | NV | Units | Range | Remarks
| 1 | Command | Command | RW |  | Enumeration | 30078 = Clear Energy Accumulators | Always returns a value of 0
21212 = Reset Max Demand
21211 = Begin New Sub-interval
16498 = Clear Pulse Counters
| 2 | System_Type | System Type | RW | NV |  | 40 = A+B+C+N
31 = A+B+C
12 = A+B+N
11 = A+B
10 = A+N
| 3 | CT_Size | CT Primary | RW | NV | Amps | 1 - 12800
| 4 | CT_Type | CT Type | RW | NV |  | 3 = 1/3V CT
4 = Rogowski
| 5 | CT_Size_Neutral | CT Primary Neutral | RW | NV | Amps | 1 - 12800
| 6 | PT_Ratio | PT Ratio | RW | NV
| 7 | System_Voltage | System Voltage | RW | NV | Volts
| 8 | Max_System_Power | Max Sytem Power | R | NV | kW
| 9 | Phase_Loss_Voltage_Threshold | Phase Loss Voltage Threshold | RW | NV | %
| 10 | Phase_Loss_Imbalance_Threshold | Phase Loss Imbalance Threshold | RW | NV | %
| 11 | Energy_Pulse_Weight | Wh Per Pulse Output | RW | NV | Wh
| 12 | Pulse_Contact_Closure_Duration | Pulse Contact Closure Duration | RW | NV | Milliseconds
| 13 | Sub-Intervals | Number of Sub-Intervals per Demand Interval | RW | NV |  | 1 - 6
| 14 | Sub-Interval_Length | SubInterval Length | RW | NV | Seconds | 0 - 32767
| 15 | CT_Input_Polarity | CT Input Polarity | RW | NV | Bitmap | xxx0b - xxx1b (bit 0) = Phase N | 0 = Normal, 1 = Reversed
xx0xb - xx1xb (bit 1) = Phase A
x0xxb - x1xxb (bit 2) = Phase B
0xxxb - 1xxxb (bit 3) = Phase C
| 16 | Voltage_Input_L1_Association | Voltage Input L1 CT Association | R | NV | Enumeration | 1 = Phase A | Default
2 = Phase B
3 = Phase C
| 17 | Voltage_Input_L2_Association | Voltage Input L2 CT Association | R | NV | Enumeration | 1 = Phase A
[7 empty] | 2 = Phase B | Default
3 = Phase C
| 18 | Voltage_Input_L3_Association | Voltage Input L3 CT Association | R | NV | Enumeration | 1 = Phase A
2 = Phase B
[7 empty] | 3 = Phase C | Default
| 19 | MAC_Address | MSTP MAC Address | RW | NV |  | 1 - 127
| 20 | MSTP_Baud | MSTP Baudrate | RW | NV |  | 9600, 19200, 38400, 76800, 115200
| 21 | Energy_Resets | Energy Resets | R | NV |  | 0 - 32767
| 22 | Power_Up_Counter | Power Up Counter | R | NV |  | 0 - 32767
| 23 | Calibration_Event_Counter | Calibration Event Counter | R | NV |  | 0 - 32767
| 24 | Configuration_Event_Counter | Configuration Event Counter | R | NV |  | 0 - 32767
| 25 | Output_Configuration | Output Configuration | R | NV |  | 0 - 32767
| 26 | Voltage_Input_To_CT_Association_General | Voltage Input to CT Association General | RW | NV |  | 123 132 231 213 321 312

## Binary Inputs
Binary Inputs | BI# | Object Name | BACnet Description | RW | NV | Additional Information
| 1 | Voltage_Error_L1 | Voltage Out of Range L1 | R
| 2 | Voltage_Error_L2 | Voltage Out of Range L2 | R
| 3 | Voltage_Error_L3 | Voltage Out of Range L3 | R
| 4 | Current_Error_L1 | Current Out of Range L1 | R
| 5 | Current_Error_L2 | Current Out of Range L2 | R
| 6 | Current_Error_L3 | Current Out of Range L3 | R
| 7 | Neutral_Current_Error | Current Out of Range Neutral | R
| 8 | Frequency_Error | Frequency Out of Range | R
| 9 | Phase_Loss_L1 | Voltage Phase Loss L1 | R
| 10 | Phase_Loss_L2 | Voltage Phase Loss L2 | R
| 11 | Phase_Loss_L3 | Voltage Phase Loss L3 | R
| 12 | Low_Power_Factor_L1 | Low Power Factor L1 | R
| 13 | Low_Power_Factor_L2 | Low Power Factor L2 | R
| 14 | Low_Power_Factor_L3 | Low Power Factor L3 | R
| 15 | Pulse_Overrun_Error | Energy Pulse Output Overrun Error | R
| 16 | Pulse_Configuration_Error | Energy Pulse Output Configuration Error | R
| 17 | CT_Size_Override | CT Primary Size Control Overridden | R
| 18 | Energy_Pulse_Weight_Override | Energy Pulse Weight Control Overridden | R
| 19 | Device_Address_Override | Device Address Control Overridden | R
| 20 | Meter_Mode_Override | Meter Mode Control Overridden | R
| 21 | Analog_Output_Control_Override | Analog Output Control Overridden | R
| 22 | CT_Interface_Override | CT Interface Overridden | R