## Instructions
NVE41316 | V3.5 | ATV320 - Communication Parameters
WARNING
UNEXPECTED MOVEMENT
Drive systems may perform unexpected movements because of incorrect wiring, incorrect settings, incorrect data or other errors. • Only appropriately trained persons who are familiar with and understand the contents of all pertinent product documentation and who have received safety training to recognize and avoid hazards involved are authorized to work on and with this drive system. Installation, adjustment, repair and maintenance must be performed by qualified personnel. • Carefully install the wiring in accordance with the EMC requirements. • Do not operate the product with unknown or unsuitable settings or data. • Perform a comprehensive commissioning test.
Failure to follow these instructions can result in death, serious injury, or equipment damage.
WARNING
LOSS OF CONTROL
• The designer of any control scheme must consider the potential failure modes of control paths and, for critical control functions, provide a means to achieve a safe state during and after a path failure. Examples of critical control functions are emergency stop, overtravel stop, power outage and restart. • Separate or redundant control paths must be provided for critical control functions. • System control paths may include communication links. Consideration must be given to the implications of unanticipated transmission delays or failures of the link. • Observe all accident prevention regulations and local safety guidelines (1). • Each implementation of the product must be individually and thoroughly tested for proper operation before being placed into service.
Failure to follow these instructions can result in death, serious injury, or equipment damage.
Note a.: For additional information, refer to NEMA ICS 1.1 (latest edition), “Safety Guidelines for the Application, Installation, and Maintenance of Solid State Control” and to NEMA ICS 7.1 (latest edition), “Safety Standards for Construction and Guide for Selection, Installation and Operation of Adjustable-Speed Drive Systems.”
Electrical equipment should be installed, operated, serviced, and maintained only by qualified personnel. No responsibility is assumed by Schneider Electric for any consequences arising out of the use of this material.
EXPLANATORY NOTE
This Excel file is for reference only. Refer to programming manual and communication protocols manuals for full information.
This Excel file can be used to carry out searches (example: parameter address and format) and sort operations.
The columns include the following criteria:
Code:
Language-independent, this allows a rapid search in the programming manual, which includes an index of parameter codes.
Additional information can be found in the Communication Manuals (Modbus, CANopen....etc.....)
Name:
Parameter designation
Logic address:
Addresses for Modbus, Profibus, Profinet and Ethernet TCP
Address for the messaging are in decimal and hexadecimal (preceded by 16#) format.
To optimize messaging performance, two addresses are given for the control word (CMD) and the status word (ETA).
The addresses annotated "speed" are for use in rpm; the addresses annotated "frequency" are for use in Hz.
CANopen index:
Addresses for CANopen, PowerLink and EtherCAT.
CANopen index/subindex in hexadecimal format, to be used for variable assignment of PDOs and SDO messaging.
DeviceNet path:
Address for DeviceNet and Ethernet IP.
Class/instance/attribute in decimal and hexadecimal (preceded by 16#) format.
When two paths are given, for example:
- 16#29/01/0D = 41/1/13 (messaging): ODVA standard path. It can be used for explicit messaging. Do not use it for configuring an assembly.
- 16#8C/01/07 = 140/1/7 (assembly): Altivar-specific path. This is the path that must be used for configuring an assembly. Avoid using it for explicit messaging, to ensure better interchangeability.
Link:
- For WORD (listing), a dynamic link opens its description. Listings are common to several parameters; only one part is valid for a given parameter. Refer to programming manual to determine the valid values. If an invalid value is written to a configuration parameter, the drive will indicate a fault [Invalid config.] (CFI).
- For WORD (bit register), in the Type column, a dynamic link opens its description.
Category:
Defines the role of the parameter, for example: Command parameter, Status parameter, etc.
Access:
Read and write options:
R: Read only
R/W: Read and write
R/WS: Read and write (write only possible when the drive is not in RUN mode).
It is not possible to write these parameters in "5-Operation enabled" or "6-Quick stop active" states.
If the parameter is written in the "4-Switched on" state, transition 10 to "2-Switch on disabled" is activated.
Type:
WORD (bit register): Word where each bit represents a command or a state
WORD (listing): Word where each value represents a possible choice for a configuration or state
INT: Signed integer
UINT: Unsigned integer
DINT: Signed double integer
UDINT: Unsigned double integer
Units:
Physical unit and multiplier.
Factory setting:
Value of the parameter set at the factory.
Menu:
Indicates the menus or menus where the parameter is located. Menu name displayed on the graphic display terminal, in square brackets [---], and menu code displayed by the 7-segment digits on the integrated display terminal, in round brackets (---).
Range:
Possible values.
Display:
Parameter name displayed on the graphic display terminal, in square brackets [---], and parameter code displayed by the 7-segment digits on the integrated display terminal, in round brackets (---).
Menu:
Indicates the menus or menus where the parameter is located. Menu name displayed on the graphic display terminal, in square brackets [---], and menu code displayed by the 7-segment digits on the integrated display terminal, in round brackets (---).
Order:
Gives the initial storage order of the parameter in the file, from 1 to n. This makes it possible, after sorting operations, to put this file back in its initial order by sorting the column in ascending order.

## Parameters
Code | Name | Logic address | CANopen index | DeviceNet path | Link | Category | Access | Type | Units | Factory setting | Range | Display | Menu
CMI | Extended control word | 16#2138 = 8504 | 16#2037/5 | 16#8B/01/69 = 139/01/105 |  | Control parameters | R/W | WORD (BitString16) | -
CMD | DrivecomCmdReg | 16#2135 = 8501 | 16#2037/2 | 16#8B/01/66 = 139/01/102 |  | Control parameters | R/W | WORD (BitString16) | - |  |  | [Cmd value] (CMD) | [COMMUNICATION MAP] (CMM)
RPR | Operating time reset | 16#0C30 = 3120 | 16#2001/15 | 16#70/01/79 = 112/01/121 | RPR | Control parameters | R/W | WORD (Enumeration) | - | [No] NO |  | [Operating t. reset] (RPR) | [MONIT. POWER TIME] (PET)
LFRD | Speed setpoint | 16#219A = 8602 | 16#2038/3 | 16#8C/01/03 = 140/01/03 |  | Setpoint parameters | R/W | INT (Signed16) | 1 rpm | 0 rpm | -32767 rpm ... 32767 rpm
LFR | Frequency reference | 16#2136 = 8502 | 16#2037/3 | 16#8B/01/67 = 139/01/103 |  | Setpoint parameters | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | -599.0 Hz ... 599.0 Hz | [Frequency ref.] (LFR) | [SPEED REFERENCE] (rEF) [MONITORING] (MON)
PISP | PID set point | 16#2137 = 8503 | 16#2037/4 | 16#8B/01/68 = 139/01/104 |  | Setpoint parameters | R/W | UINT (Unsigned16) | 1 |  | 0 ... 1000
AIV1 | Image input AIV1 | 16#14A1 = 5281 | 16#2016/52 | 16#7B/01/52 = 123/01/82 |  | Setpoint parameters | R/W | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Image input AIV1] (AIV1) | [SPEED REFERENCE] (rEF) [MONITORING] (MON)
MFR | Multiplying coefficient | 16#2E37 = 11831 | 16#2058/20 | 16#9C/01/20 = 156/01/32 |  | Setpoint parameters | R/W | UINT (Unsigned16) | 1 % |  | 0 % ... 100 % | [Multiplying coeff.] (MFR) | [SPEED REFERENCE] (rEF) [MONITORING] (MON) [SETTINGS] (SET)
ETA | Drivecom state register | 16#0C81 = 3201 | 16#2002/2 | 16#71/01/02 = 113/01/02 |  | Status parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (ETA) | [COMMUNICATION MAP] (CMM)
HMIS | Drive state | 16#0CA8 = 3240 | 16#2002/29 | 16#71/01/29 = 113/01/41 | HMIS | Status parameters | R | WORD (Enumeration) | -
ETI | Extended state register | 16#0C86 = 3206 | 16#2002/7 | 16#71/01/07 = 113/01/07 |  | Status parameters | R | WORD (BitString16) | -
CRC | Reference channel | 16#20F9 = 8441 | 16#2036/2A | 16#8B/01/2A = 139/01/42 |  | Status parameters | R | WORD (BitString16) | -
CCC | Active command channel | 16#20FA = 8442 | 16#2036/2B | 16#8B/01/2B = 139/01/43 |  | Status parameters | R | WORD (BitString16) | -
CNFS | Active configuration | 16#1F54 = 8020 | 16#2032/15 | 16#89/01/15 = 137/01/21 | CNFS | Status parameters | R | WORD (Enumeration) | - |  |  | [Config. active] (CNFS) | [MONITORING] (MON)
STUN | Tune selection | 16#2591 = 9617 | 16#2042/12 | 16#91/01/12 = 145/01/18 | STUN | Status parameters | R | WORD (Enumeration) | - | [Default] TAB |  | [Tune selection] (STUN) | [SIMPLY START] (SIM) [ASYNC. MOTOR] (ASY) [SYNCHRONOUS MOTOR] (SYN)
SMOT | Status of motor tune in term of saliency | 16#25AD = 9645 | 16#2042/2E | 16#91/01/2E = 145/01/46 | SMOT | Status parameters | R | WORD (Enumeration) | - |  |  | [Saliency mot. state] (SMOT) | [SYNCHRONOUS MOTOR] (SYN)
ECSS | EtherCAT slave status | 16#1A22 = 6690 | 16#2024/5B | 16#82/01/5B = 130/01/91 | ETST | Status parameters | R/W | WORD (Enumeration) | - |  |  | [EthCat slave status] (ECSS) | [COMMUNICATION CARD] (CBD)
ECAA | EtherCAT address | 16#1A24 = 6692 | 16#2024/5D | 16#82/01/5D = 130/01/93 |  | Status parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [EthCat addr] (ECAA) | [COMMUNICATION CARD] (CBD)
RFRD | Output velocity | 16#219C = 8604 | 16#2038/5 | 16#8C/01/05 = 140/01/05 |  | Actual values parameters | R | INT (Signed16) | 1 rpm |  | -32767 rpm ... 32767 rpm
RFR | Output frequency | 16#0C82 = 3202 | 16#2002/3 | 16#71/01/03 = 113/01/03 |  | Actual values parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFR) | [MONITORING] (MON)
OTR | Motor torque | 16#0C85 = 3205 | 16#2002/6 | 16#71/01/06 = 113/01/06 |  | Actual values parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor torque] (OTR) | [MONIT. MOTOR] (MMO)
LCR | Motor current | 16#0C84 = 3204 | 16#2002/5 | 16#71/01/05 = 113/01/05 |  | Actual values parameters | R | UINT (Unsigned16) | 0.1 A |  | 0.0 A ... 6553.5 A | [Motor current] (LCR) | [MONIT. MOTOR] (MMO)
UOP | Motor voltage | 16#0C88 = 3208 | 16#2002/9 | 16#71/01/09 = 113/01/09 |  | Actual values parameters | R | UINT (Unsigned16) | 1 V |  | 0 V ... 65535 V | [Motor voltage] (UOP) | [MONIT. MOTOR] (MMO)
OPR | Motor power | 16#0C8B = 3211 | 16#2002/C | 16#71/01/0C = 113/01/12 |  | Actual values parameters | R | INT (Signed16) | 1 % |  | -32767 % ... 32767 % | [Motor power] (OPR) | [MONIT. MOTOR] (MMO)
FRHD | Speed reference before ramp | 16#219D = 8605 | 16#2038/6 | 16#8C/01/06 = 140/01/06 |  | Reference parameters | R | INT (Signed16) | 1 rpm |  | -32767 rpm ... 32767 rpm
FROD | Speed reference after ramp | 16#21C1 = 8641 | 16#2038/2A | 16#8C/01/2A = 140/01/42 |  | Reference parameters | R | INT (Signed16) | 1 rpm |  | -32767 rpm ... 32767 rpm
FRH | Freq. ref. before ramp | 16#0C83 = 3203 | 16#2002/4 | 16#71/01/04 = 113/01/04 |  | Reference parameters | R | INT (Signed16) | 0.1 Hz |  | -599.0 Hz ... 599.0 Hz | [Frequency ref.] (FRH) | [SPEED REFERENCE] (rEF) [MONITORING] (MON) [COMMUNICATION MAP] (CMM)
FRO | Frequency reference after ramp | 16#233D = 9021 | 16#203C/16 | 16#8E/01/16 = 142/01/22 |  | Reference parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz
RPC | PID reference | 16#2ECE = 11982 | 16#2059/53 | 16#9C/01/B7 = 156/01/183 |  | Reference parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [PID reference] (RPC) | [SPEED REFERENCE] (rEF) [MONIT. PI ] (MPI)
RPF | PID feedback | 16#2ECD = 11981 | 16#2059/52 | 16#9C/01/B6 = 156/01/182 |  | Reference parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [PID feedback] (RPF) | [MONIT. PI ] (MPI)
RPE | PID error | 16#2ECC = 11980 | 16#2059/51 | 16#9C/01/B5 = 156/01/181 |  | Reference parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767 | [PID error] (RPE) | [MONIT. PI ] (MPI)
RPO | PID Output | 16#2ECF = 11983 | 16#2059/54 | 16#9C/01/B8 = 156/01/184 |  | Reference parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [PID Output] (RPO) | [MONIT. PI ] (MPI)
ULN | Line mains voltage | 16#0C87 = 3207 | 16#2002/8 | 16#71/01/08 = 113/01/08 |  | Measurement parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [Mains voltage] (ULN) | [MONITORING] (MON)
THD | Drive thermal state | 16#0C89 = 3209 | 16#2002/A | 16#71/01/0A = 113/01/10 |  | Measurement parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 % | [Drv. thermal state] (THD) | [MONITORING] (MON)
THR | Motor thermal state | 16#259E = 9630 | 16#2042/1F | 16#91/01/1F = 145/01/31 |  | Measurement parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 % | [Motor thermal state] (THR) | [MONITORING] (MON)
RTH | Motor run time | 16#0C9F = 3231 | 16#2002/20 | 16#71/01/20 = 113/01/32 |  | Measurement parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Run time] (RTH) | [MONIT. POWER TIME] (PET)
PTH | Power on time | 16#0CA1 = 3233 | 16#2002/22 | 16#71/01/22 = 113/01/34 |  | Measurement parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Power on time] (PTH) | [MONIT. POWER TIME] (PET)
IL1R | Logic inputs states | 16#1452 = 5202 | 16#2016/3 | 16#7B/01/03 = 123/01/03 |  | I/O parameters | R | WORD (BitString16) | -
OL1R | Logic outputs states | 16#145C = 5212 | 16#2016/D | 16#7B/01/0D = 123/01/13 |  | I/O parameters | R/W | WORD (BitString16) | -
AI1C | Physical value AI1 | 16#147A = 5242 | 16#2016/2B | 16#7B/01/2B = 123/01/43 |  | I/O parameters | R | INT (Signed16) | 0.001 V |  | -32.767 V ... 32.767 V
AI1R | Analog input 1 standardized value | 16#1470 = 5232 | 16#2016/21 | 16#7B/01/21 = 123/01/33 |  | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AI2C | Physical value AI2 | 16#147B = 5243 | 16#2016/2C | 16#7B/01/2C = 123/01/44 |  | I/O parameters | R | INT (Signed16) | 0.001 V |  | -32.767 V ... 32.767 V
AI2R | Analog input 2 standardized value | 16#1471 = 5233 | 16#2016/22 | 16#7B/01/22 = 123/01/34 |  | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AI3C | Physical value AI3 | 16#147C = 5244 | 16#2016/2D | 16#7B/01/2D = 123/01/45 |  | I/O parameters | R | INT (Signed16) | 0.001 mA |  | -32.767 mA ... 32.767 mA
AI3R | Analog input 3 standardized value | 16#1472 = 5234 | 16#2016/23 | 16#7B/01/23 = 123/01/35 |  | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AO1C | AO1 physical value | 16#1497 = 5271 | 16#2016/48 | 16#7B/01/48 = 123/01/72 |  | I/O parameters | R/W | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
FQS | Pulse input working freq. | 16#390B = 14603 | 16#2074/4 | 16#AA/01/04 = 170/01/04 |  | I/O parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 20000 Hz | [Pulse in. work. freq.] (FQS) | [MONITORING] (MON)
AO1R | Analog output 1 standardized value | 16#148D = 5261 | 16#2016/3E | 16#7B/01/3E = 123/01/62 |  | I/O parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
ERRD | CiA402 fault code | 16#219E = 8606 | 16#2038/7 | 16#8C/01/07 = 140/01/07 | ERRD | Fault parameters | R | WORD (BitString16) | -
LFT | Last fault occurred | 16#1BD1 = 7121 | 16#2029/16 | 16#84/01/7A = 132/01/122 | LFT | Fault parameters | R | WORD (Enumeration) | -
CIC | Incorrect configuration | 16#1BDA = 7130 | 16#2029/1F | 16#84/01/83 = 132/01/131 |  | Fault parameters | R/WS | WORD (BitString16) | -
CNF | Comm. option fault | 16#1BDC = 7132 | 16#2029/21 | 16#84/01/85 = 132/01/133 |  | Fault parameters | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Network fault] (CNF) | [MORE FAULT INFO] (AFI) [COMMUNICATION CARD] (CBD)
ILF1 | Internal link fault 1 | 16#1BDE = 7134 | 16#2029/23 | 16#84/01/87 = 132/01/135 |  | Fault parameters | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Internal link fault 1] (ILF1) | [MORE FAULT INFO] (AFI) [COMMUNICATION CARD] (CBD)
FNB | Fault counter | 16#1CE1 = 7393 | 16#202B/5E | 16#85/01/C2 = 133/01/194 |  | Fault parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DP0 | Fault code on last fault | 16#1C20 = 7200 | 16#202A/1 | 16#85/01/01 = 133/01/01 | LFT | History parameters | R | WORD (Enumeration) | -
ULP0 | Mains voltage | 16#1C66 = 7270 | 16#202A/47 | 16#85/01/47 = 133/01/71 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V
LCP0 | Motor current | 16#1C48 = 7240 | 16#202A/29 | 16#85/01/29 = 133/01/41 |  | History parameters | R | INT (Signed16) | 0.1 A |  | -3276.7 A ... 3276.7 A
RFP0 | Output frequency | 16#1C52 = 7250 | 16#202A/33 | 16#85/01/33 = 133/01/51 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz
THP0 | Motor thermal state | 16#1C70 = 7280 | 16#202A/51 | 16#85/01/51 = 133/01/81 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 %
EP0 | State word | 16#1C2A = 7210 | 16#202A/B | 16#85/01/0B = 133/01/11 |  | History parameters | R | WORD (BitString16) | -
IP0 | ETI state word | 16#1C34 = 7220 | 16#202A/15 | 16#85/01/15 = 133/01/21 |  | History parameters | R | WORD (BitString16) | -
CMP0 | Cmd word | 16#1C3E = 7230 | 16#202A/1F | 16#85/01/1F = 133/01/31 |  | History parameters | R | WORD (BitString16) | -
DCC0 | Command channel | 16#FB2C = 64300 |  |  | CNL | History parameters | R | WORD (Enumeration) | -
DRC0 | Reference channel | 16#FB36 = 64310 |  |  | CNL | History parameters | R | WORD (Enumeration) | -
CRP0 | Channels active on last fault | 16#1C7A = 7290 | 16#202A/5B | 16#85/01/5B = 133/01/91 |  | History parameters | R | WORD (BitString16) | -
RTP0 | Elapsed time | 16#1C5C = 7260 | 16#202A/3D | 16#85/01/3D = 133/01/61 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h
OTP0 | Estimated motor torque value of actual fault | 16#1CA2 = 7330 | 16#202B/1F | 16#85/01/83 = 133/01/131 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 %
TDP0 | Mesured drive thermal state of actual fault | 16#1CAC = 7340 | 16#202B/29 | 16#85/01/8D = 133/01/141 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 %
TJP0 | Estimated TJ value of actual fault | 16#1CB6 = 7350 | 16#202B/33 | 16#85/01/97 = 133/01/151 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C
SFP0 | Switching frequency really applied by MotorControl of actual fault | 16#1CC0 = 7360 | 16#202B/3D | 16#85/01/A1 = 133/01/161 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz
DP1 | Fault code on fault n-1 | 16#1C21 = 7201 | 16#202A/2 | 16#85/01/02 = 133/01/02 | LFT | History parameters | R | WORD (Enumeration) | -
ULP1 | Mains voltage | 16#1C67 = 7271 | 16#202A/48 | 16#85/01/48 = 133/01/72 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [Mains voltage] (ULP1) | [None] (DP1)
LCP1 | Motor current | 16#1C49 = 7241 | 16#202A/2A | 16#85/01/2A = 133/01/42 |  | History parameters | R | INT (Signed16) | 0.1 A |  | -3276.7 A ... 3276.7 A | [Motor current] (LCP1) | [None] (DP1)
RFP1 | Output frequency | 16#1C53 = 7251 | 16#202A/34 | 16#85/01/34 = 133/01/52 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP1) | [None] (DP1)
THP1 | Motor thermal state | 16#1C71 = 7281 | 16#202A/52 | 16#85/01/52 = 133/01/82 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor thermal state] (THP1) | [None] (DP1)
EP1 | State word | 16#1C2B = 7211 | 16#202A/C | 16#85/01/0C = 133/01/12 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EP1) | [None] (DP1)
IP1 | ETI state word | 16#1C35 = 7221 | 16#202A/16 | 16#85/01/16 = 133/01/22 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP1) | [None] (DP1)
CMP1 | Cmd word | 16#1C3F = 7231 | 16#202A/20 | 16#85/01/20 = 133/01/32 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP1) | [None] (DP1)
DCC1 | Command channel | 16#FB2D = 64301 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC1) | [None] (DP1)
DRC1 | Reference channel | 16#FB37 = 64311 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Channel ref. active] (DRC1) | [None] (DP1)
CRP1 | Active channels on fault n-1 | 16#1C7B = 7291 | 16#202A/5C | 16#85/01/5C = 133/01/92 |  | History parameters | R | WORD (BitString16) | -
RTP1 | Elapsed time | 16#1C5D = 7261 | 16#202A/3E | 16#85/01/3E = 133/01/62 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Elapsed time] (RTP1) | [None] (DP1)
OTP1 | Estimated motor torque value of fault record x (1 is last) | 16#1CA3 = 7331 | 16#202B/20 | 16#85/01/84 = 133/01/132 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 %
TDP1 | Mesured drive thermal state of fault record x (1 is last) | 16#1CAD = 7341 | 16#202B/2A | 16#85/01/8E = 133/01/142 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 %
TJP1 | Estimated TJ value of fault record x (1 is last) | 16#1CB7 = 7351 | 16#202B/34 | 16#85/01/98 = 133/01/152 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C
SFP1 | Switching frequency really applied by MotorControl of fault record x (1 is last) | 16#1CC1 = 7361 | 16#202B/3E | 16#85/01/A2 = 133/01/162 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz
DP2 | Fault code on fault n-2 | 16#1C22 = 7202 | 16#202A/3 | 16#85/01/03 = 133/01/03 | LFT | History parameters | R | WORD (Enumeration) | -
ULP2 | Mains voltage | 16#1C68 = 7272 | 16#202A/49 | 16#85/01/49 = 133/01/73 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [Mains voltage] (ULP2) | [None] (DP2)
LCP2 | Motor current | 16#1C4A = 7242 | 16#202A/2B | 16#85/01/2B = 133/01/43 |  | History parameters | R | INT (Signed16) | 0.1 A |  | -3276.7 A ... 3276.7 A | [Motor current] (LCP2) | [None] (DP2)
RFP2 | Output frequency | 16#1C54 = 7252 | 16#202A/35 | 16#85/01/35 = 133/01/53 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP2) | [None] (DP2)
THP2 | Motor thermal state | 16#1C72 = 7282 | 16#202A/53 | 16#85/01/53 = 133/01/83 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor thermal state] (THP2) | [None] (DP2)
EP2 | State word | 16#1C2C = 7212 | 16#202A/D | 16#85/01/0D = 133/01/13 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EP2) | [None] (DP2)
IP2 | ETI state word | 16#1C36 = 7222 | 16#202A/17 | 16#85/01/17 = 133/01/23 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP2) | [None] (DP2)
CMP2 | Cmd word | 16#1C40 = 7232 | 16#202A/21 | 16#85/01/21 = 133/01/33 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP2) | [None] (DP2)
DCC2 | Command channel | 16#FB2E = 64302 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC2) | [None] (DP2)
DRC2 | Reference channel | 16#FB38 = 64312 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Channel ref. active] (DRC2) | [None] (DP2)
CRP2 | Active channels on fault n-2 | 16#1C7C = 7292 | 16#202A/5D | 16#85/01/5D = 133/01/93 |  | History parameters | R | WORD (BitString16) | -
RTP2 | Elapsed time | 16#1C5E = 7262 | 16#202A/3F | 16#85/01/3F = 133/01/63 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Elapsed time] (RTP2) | [None] (DP2)
OTP2 | Estimated motor torque value of fault record x (1 is last) | 16#1CA4 = 7332 | 16#202B/21 | 16#85/01/85 = 133/01/133 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 %
TDP2 | Mesured drive thermal state of fault record x (1 is last) | 16#1CAE = 7342 | 16#202B/2B | 16#85/01/8F = 133/01/143 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 %
TJP2 | Estimated TJ value of fault record x (1 is last) | 16#1CB8 = 7352 | 16#202B/35 | 16#85/01/99 = 133/01/153 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C
SFP2 | Switching frequency really applied by MotorControl of fault record x (1 is last) | 16#1CC2 = 7362 | 16#202B/3F | 16#85/01/A3 = 133/01/163 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz
DP3 | Fault code on fault n-3 | 16#1C23 = 7203 | 16#202A/4 | 16#85/01/04 = 133/01/04 | LFT | History parameters | R | WORD (Enumeration) | -
ULP3 | Mains voltage | 16#1C69 = 7273 | 16#202A/4A | 16#85/01/4A = 133/01/74 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [Mains voltage] (ULP3) | [None] (DP3)
LCP3 | Motor current | 16#1C4B = 7243 | 16#202A/2C | 16#85/01/2C = 133/01/44 |  | History parameters | R | INT (Signed16) | 0.1 A |  | -3276.7 A ... 3276.7 A | [Motor current] (LCP3) | [None] (DP3)
RFP3 | Output frequency | 16#1C55 = 7253 | 16#202A/36 | 16#85/01/36 = 133/01/54 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP3) | [None] (DP3)
THP3 | Motor thermal state | 16#1C73 = 7283 | 16#202A/54 | 16#85/01/54 = 133/01/84 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor thermal state] (THP3) | [None] (DP3)
EP3 | State word | 16#1C2D = 7213 | 16#202A/E | 16#85/01/0E = 133/01/14 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EP3) | [None] (DP3)
IP3 | ETI state word | 16#1C37 = 7223 | 16#202A/18 | 16#85/01/18 = 133/01/24 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP3) | [None] (DP3)
CMP3 | Cmd word | 16#1C41 = 7233 | 16#202A/22 | 16#85/01/22 = 133/01/34 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP3) | [None] (DP3)
DCC3 | Command channel | 16#FB2F = 64303 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC3) | [None] (DP3)
DRC3 | Reference channel | 16#FB39 = 64313 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Channel ref. active] (DRC3) | [None] (DP3)
CRP3 | Active channels on fault n-3 | 16#1C7D = 7293 | 16#202A/5E | 16#85/01/5E = 133/01/94 |  | History parameters | R | WORD (BitString16) | -
RTP3 | Elapsed time | 16#1C5F = 7263 | 16#202A/40 | 16#85/01/40 = 133/01/64 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Elapsed time] (RTP3) | [None] (DP3)
OTP3 | Estimated motor torque value of fault record x (1 is last) | 16#1CA5 = 7333 | 16#202B/22 | 16#85/01/86 = 133/01/134 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 %
TDP3 | Mesured drive thermal state of fault record x (1 is last) | 16#1CAF = 7343 | 16#202B/2C | 16#85/01/90 = 133/01/144 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 %
TJP3 | Estimated TJ value of fault record x (1 is last) | 16#1CB9 = 7353 | 16#202B/36 | 16#85/01/9A = 133/01/154 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C
SFP3 | Switching frequency really applied by MotorControl of fault record x (1 is last) | 16#1CC3 = 7363 | 16#202B/40 | 16#85/01/A4 = 133/01/164 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz
DP4 | Fault code on fault n-4 | 16#1C24 = 7204 | 16#202A/5 | 16#85/01/05 = 133/01/05 | LFT | History parameters | R | WORD (Enumeration) | -
ULP4 | Mains voltage | 16#1C6A = 7274 | 16#202A/4B | 16#85/01/4B = 133/01/75 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [Mains voltage] (ULP4) | [None] (DP4)
LCP4 | Motor current | 16#1C4C = 7244 | 16#202A/2D | 16#85/01/2D = 133/01/45 |  | History parameters | R | INT (Signed16) | 0.1 A |  | -3276.7 A ... 3276.7 A | [Motor current] (LCP4) | [None] (DP4)
RFP4 | Output frequency | 16#1C56 = 7254 | 16#202A/37 | 16#85/01/37 = 133/01/55 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP4) | [None] (DP4)
THP4 | Motor thermal state | 16#1C74 = 7284 | 16#202A/55 | 16#85/01/55 = 133/01/85 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor thermal state] (THP4) | [None] (DP4)
EP4 | State word | 16#1C2E = 7214 | 16#202A/F | 16#85/01/0F = 133/01/15 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EP4) | [None] (DP4)
IP4 | ETI state word | 16#1C38 = 7224 | 16#202A/19 | 16#85/01/19 = 133/01/25 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP4) | [None] (DP4)
CMP4 | Cmd word | 16#1C42 = 7234 | 16#202A/23 | 16#85/01/23 = 133/01/35 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP4) | [None] (DP4)
DCC4 | Command channel | 16#FB30 = 64304 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC4) | [None] (DP4)
DRC4 | Reference channel | 16#FB3A = 64314 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Channel ref. active] (DRC4) | [None] (DP4)
CRP4 | Active channels on fault n-4 | 16#1C7E = 7294 | 16#202A/5F | 16#85/01/5F = 133/01/95 |  | History parameters | R | WORD (BitString16) | -
RTP4 | Elapsed time | 16#1C60 = 7264 | 16#202A/41 | 16#85/01/41 = 133/01/65 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Elapsed time] (RTP4) | [None] (DP4)
OTP4 | Estimated motor torque value of fault record x (1 is last) | 16#1CA6 = 7334 | 16#202B/23 | 16#85/01/87 = 133/01/135 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 %
TDP4 | Mesured drive thermal state of fault record x (1 is last) | 16#1CB0 = 7344 | 16#202B/2D | 16#85/01/91 = 133/01/145 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 %
TJP4 | Estimated TJ value of fault record x (1 is last) | 16#1CBA = 7354 | 16#202B/37 | 16#85/01/9B = 133/01/155 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C
SFP4 | Switching frequency really applied by MotorControl of fault record x (1 is last) | 16#1CC4 = 7364 | 16#202B/41 | 16#85/01/A5 = 133/01/165 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz
DP5 | Fault code on fault n-5 | 16#1C25 = 7205 | 16#202A/6 | 16#85/01/06 = 133/01/06 | LFT | History parameters | R | WORD (Enumeration) | -
ULP5 | Mains voltage | 16#1C6B = 7275 | 16#202A/4C | 16#85/01/4C = 133/01/76 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [Mains voltage] (ULP5) | [None] (DP5)
LCP5 | Motor current | 16#1C4D = 7245 | 16#202A/2E | 16#85/01/2E = 133/01/46 |  | History parameters | R | INT (Signed16) | 0.1 A |  | -3276.7 A ... 3276.7 A | [Motor current] (LCP5) | [None] (DP5)
RFP5 | Output frequency | 16#1C57 = 7255 | 16#202A/38 | 16#85/01/38 = 133/01/56 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP5) | [None] (DP5)
THP5 | Motor thermal state | 16#1C75 = 7285 | 16#202A/56 | 16#85/01/56 = 133/01/86 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor thermal state] (THP5) | [None] (DP5)
EP5 | State word | 16#1C2F = 7215 | 16#202A/10 | 16#85/01/10 = 133/01/16 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EP5) | [None] (DP5)
IP5 | ETI state word | 16#1C39 = 7225 | 16#202A/1A | 16#85/01/1A = 133/01/26 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP5) | [None] (DP5)
CMP5 | Cmd word | 16#1C43 = 7235 | 16#202A/24 | 16#85/01/24 = 133/01/36 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP5) | [None] (DP5)
DCC5 | Command channel | 16#FB31 = 64305 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC5) | [None] (DP5)
DRC5 | Reference channel | 16#FB3B = 64315 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Channel ref. active] (DRC5) | [None] (DP5)
CRP5 | Active channels on fault n-5 | 16#1C7F = 7295 | 16#202A/60 | 16#85/01/60 = 133/01/96 |  | History parameters | R | WORD (BitString16) | -
RTP5 | Elapsed time | 16#1C61 = 7265 | 16#202A/42 | 16#85/01/42 = 133/01/66 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Elapsed time] (RTP5) | [None] (DP5)
OTP5 | Estimated motor torque value of fault record x (1 is last) | 16#1CA7 = 7335 | 16#202B/24 | 16#85/01/88 = 133/01/136 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 %
TDP5 | Mesured drive thermal state of fault record x (1 is last) | 16#1CB1 = 7345 | 16#202B/2E | 16#85/01/92 = 133/01/146 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 %
TJP5 | Estimated TJ value of fault record x (1 is last) | 16#1CBB = 7355 | 16#202B/38 | 16#85/01/9C = 133/01/156 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C
SFP5 | Switching frequency really applied by MotorControl of fault record x (1 is last) | 16#1CC5 = 7365 | 16#202B/42 | 16#85/01/A6 = 133/01/166 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz
DP6 | Fault code on fault n-6 | 16#1C26 = 7206 | 16#202A/7 | 16#85/01/07 = 133/01/07 | LFT | History parameters | R | WORD (Enumeration) | -
ULP6 | Mains voltage | 16#1C6C = 7276 | 16#202A/4D | 16#85/01/4D = 133/01/77 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [Mains voltage] (ULP6) | [None] (DP6)
LCP6 | Motor current | 16#1C4E = 7246 | 16#202A/2F | 16#85/01/2F = 133/01/47 |  | History parameters | R | INT (Signed16) | 0.1 A |  | -3276.7 A ... 3276.7 A | [Motor current] (LCP6) | [None] (DP6)
RFP6 | Output frequency | 16#1C58 = 7256 | 16#202A/39 | 16#85/01/39 = 133/01/57 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP6) | [None] (DP6)
THP6 | Motor thermal state | 16#1C76 = 7286 | 16#202A/57 | 16#85/01/57 = 133/01/87 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor thermal state] (THP6) | [None] (DP6)
EP6 | State word | 16#1C30 = 7216 | 16#202A/11 | 16#85/01/11 = 133/01/17 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EP6) | [None] (DP6)
IP6 | ETI state word | 16#1C3A = 7226 | 16#202A/1B | 16#85/01/1B = 133/01/27 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP6) | [None] (DP6)
CMP6 | Cmd word | 16#1C44 = 7236 | 16#202A/25 | 16#85/01/25 = 133/01/37 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP6) | [None] (DP6)
DCC6 | Command channel | 16#FB32 = 64306 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC6) | [None] (DP6)
DRC6 | Reference channel | 16#FB3C = 64316 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Channel ref. active] (DRC6) | [None] (DP6)
CRP6 | Active channels on fault n-6 | 16#1C80 = 7296 | 16#202A/61 | 16#85/01/61 = 133/01/97 |  | History parameters | R | WORD (BitString16) | -
RTP6 | Elapsed time | 16#1C62 = 7266 | 16#202A/43 | 16#85/01/43 = 133/01/67 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Elapsed time] (RTP6) | [None] (DP6)
OTP6 | Estimated motor torque value of fault record x (1 is last) | 16#1CA8 = 7336 | 16#202B/25 | 16#85/01/89 = 133/01/137 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 %
TDP6 | Mesured drive thermal state of fault record x (1 is last) | 16#1CB2 = 7346 | 16#202B/2F | 16#85/01/93 = 133/01/147 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 %
TJP6 | Estimated TJ value of fault record x (1 is last) | 16#1CBC = 7356 | 16#202B/39 | 16#85/01/9D = 133/01/157 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C
SFP6 | Switching frequency really applied by MotorControl of fault record x (1 is last) | 16#1CC6 = 7366 | 16#202B/43 | 16#85/01/A7 = 133/01/167 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz
DP7 | Fault code on fault n-7 | 16#1C27 = 7207 | 16#202A/8 | 16#85/01/08 = 133/01/08 | LFT | History parameters | R | WORD (Enumeration) | -
ULP7 | Mains voltage | 16#1C6D = 7277 | 16#202A/4E | 16#85/01/4E = 133/01/78 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [Mains voltage] (ULP7) | [None] (DP7)
LCP7 | Motor current | 16#1C4F = 7247 | 16#202A/30 | 16#85/01/30 = 133/01/48 |  | History parameters | R | INT (Signed16) | 0.1 A |  | -3276.7 A ... 3276.7 A | [Motor current] (LCP7) | [None] (DP7)
RFP7 | Output frequency | 16#1C59 = 7257 | 16#202A/3A | 16#85/01/3A = 133/01/58 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP7) | [None] (DP7)
THP7 | Motor thermal state | 16#1C77 = 7287 | 16#202A/58 | 16#85/01/58 = 133/01/88 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor thermal state] (THP7) | [None] (DP7)
EP7 | State word | 16#1C31 = 7217 | 16#202A/12 | 16#85/01/12 = 133/01/18 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EP7) | [None] (DP7)
IP7 | ETI state word | 16#1C3B = 7227 | 16#202A/1C | 16#85/01/1C = 133/01/28 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP7) | [None] (DP7)
CMP7 | Cmd word | 16#1C45 = 7237 | 16#202A/26 | 16#85/01/26 = 133/01/38 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP7) | [None] (DP7)
DCC7 | Command channel | 16#FB33 = 64307 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC7) | [None] (DP7)
DRC7 | Reference channel | 16#FB3D = 64317 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Channel ref. active] (DRC7) | [None] (DP7)
CRP7 | Active channels on fault n-7 | 16#1C81 = 7297 | 16#202A/62 | 16#85/01/62 = 133/01/98 |  | History parameters | R | WORD (BitString16) | -
RTP7 | Elapsed time | 16#1C63 = 7267 | 16#202A/44 | 16#85/01/44 = 133/01/68 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Elapsed time] (RTP7) | [None] (DP7)
OTP7 | Estimated motor torque value of fault record x (1 is last) | 16#1CA9 = 7337 | 16#202B/26 | 16#85/01/8A = 133/01/138 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 %
TDP7 | Mesured drive thermal state of fault record x (1 is last) | 16#1CB3 = 7347 | 16#202B/30 | 16#85/01/94 = 133/01/148 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 %
TJP7 | Estimated TJ value of fault record x (1 is last) | 16#1CBD = 7357 | 16#202B/3A | 16#85/01/9E = 133/01/158 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C
SFP7 | Switching frequency really applied by MotorControl of fault record x (1 is last) | 16#1CC7 = 7367 | 16#202B/44 | 16#85/01/A8 = 133/01/168 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz
DP8 | Fault code on fault n-8 | 16#1C28 = 7208 | 16#202A/9 | 16#85/01/09 = 133/01/09 | LFT | History parameters | R | WORD (Enumeration) | -
ULP8 | Mains voltage | 16#1C6E = 7278 | 16#202A/4F | 16#85/01/4F = 133/01/79 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [Mains voltage] (ULP8) | [None] (DP8)
LCP8 | Motor current | 16#1C50 = 7248 | 16#202A/31 | 16#85/01/31 = 133/01/49 |  | History parameters | R | INT (Signed16) | 0.1 A |  | -3276.7 A ... 3276.7 A | [Motor current] (LCP8) | [None] (DP8)
RFP8 | Output frequency | 16#1C5A = 7258 | 16#202A/3B | 16#85/01/3B = 133/01/59 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP8) | [None] (DP8)
THP8 | Motor thermal state | 16#1C78 = 7288 | 16#202A/59 | 16#85/01/59 = 133/01/89 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor thermal state] (THP8) | [None] (DP8)
EP8 | State word | 16#1C32 = 7218 | 16#202A/13 | 16#85/01/13 = 133/01/19 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EP8) | [None] (DP8)
IP8 | ETI state word | 16#1C3C = 7228 | 16#202A/1D | 16#85/01/1D = 133/01/29 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP8) | [None] (DP8)
CMP8 | Cmd word | 16#1C46 = 7238 | 16#202A/27 | 16#85/01/27 = 133/01/39 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP8) | [None] (DP8)
DCC8 | Command channel | 16#FB34 = 64308 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC8) | [None] (DP8)
DRC8 | Reference channel | 16#FB3E = 64318 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Channel ref. active] (DRC8) | [None] (DP8)
CRP8 | Active channels on fault n-8 | 16#1C82 = 7298 | 16#202A/63 | 16#85/01/63 = 133/01/99 |  | History parameters | R | WORD (BitString16) | -
RTP8 | Elapsed time | 16#1C64 = 7268 | 16#202A/45 | 16#85/01/45 = 133/01/69 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Elapsed time] (RTP8) | [None] (DP8)
OTP8 | Estimated motor torque value of fault record x (1 is last) | 16#1CAA = 7338 | 16#202B/27 | 16#85/01/8B = 133/01/139 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 %
TDP8 | Mesured drive thermal state of fault record x (1 is last) | 16#1CB4 = 7348 | 16#202B/31 | 16#85/01/95 = 133/01/149 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 %
TJP8 | Estimated TJ value of fault record x (1 is last) | 16#1CBE = 7358 | 16#202B/3B | 16#85/01/9F = 133/01/159 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C
SFP8 | Switching frequency really applied by MotorControl of fault record x (1 is last) | 16#1CC8 = 7368 | 16#202B/45 | 16#85/01/A9 = 133/01/169 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz
NCV | Drive nominal rating | 16#0BC3 = 3011 | 16#2000/C | 16#70/01/0C = 112/01/12 | NCV | Identification parameters | R | WORD (Enumeration) | - | [Unknown rating] NO
VCAL | Drive mains voltage | 16#0BC4 = 3012 | 16#2000/D | 16#70/01/0D = 112/01/13 | VCAL | Identification parameters | R | WORD (Enumeration) | - | [Unknown drive rate volt.] NO
INV | Drive nominal current | 16#0BC9 = 3017 | 16#2000/12 | 16#70/01/12 = 112/01/18 |  | Identification parameters | R | UINT (Unsigned16) | 0.1 A | Refer to programming manual | 0.0 A ... 6553.5 A
VDP | Drive software version | 16#0CE6 = 3302 | 16#2003/3 | 16#71/01/67 = 113/01/103 |  | Identification parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
PAN0 | Device name (char 1 and 2) | 16#0D0C = 3340 | 16#2003/29 | 16#71/01/8D = 113/01/141 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN1 | Device name (char 3 and 4) | 16#0D0D = 3341 | 16#2003/2A | 16#71/01/8E = 113/01/142 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN2 | Device name (char 5 and 6) | 16#0D0E = 3342 | 16#2003/2B | 16#71/01/8F = 113/01/143 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN3 | Device name (char 7 and 8) | 16#0D0F = 3343 | 16#2003/2C | 16#71/01/90 = 113/01/144 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN4 | Device name (char 9 and 10) | 16#0D10 = 3344 | 16#2003/2D | 16#71/01/91 = 113/01/145 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN5 | Device name (char 11 and 12) | 16#0D11 = 3345 | 16#2003/2E | 16#71/01/92 = 113/01/146 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN6 | Device name (char 13 and 14) | 16#0D12 = 3346 | 16#2003/2F | 16#71/01/93 = 113/01/147 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN7 | Device name (char 15 and 16) | 16#0D13 = 3347 | 16#2003/30 | 16#71/01/94 = 113/01/148 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NC1 | Com scan output 1 value | 16#31D9 = 12761 | 16#2061/3E | 16#A0/01/A2 = 160/01/162 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out1 val.] (NC1) | [COM SCAN OUTPUT MAP] (OSA)
NC2 | Com scan output 2 value | 16#31DA = 12762 | 16#2061/3F | 16#A0/01/A3 = 160/01/163 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out2 val.] (NC2) | [COM SCAN OUTPUT MAP] (OSA)
NC3 | Com scan output 3 value | 16#31DB = 12763 | 16#2061/40 | 16#A0/01/A4 = 160/01/164 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out3 val.] (NC3) | [COM SCAN OUTPUT MAP] (OSA)
NC4 | Com scan output 4 value | 16#31DC = 12764 | 16#2061/41 | 16#A0/01/A5 = 160/01/165 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out4 val.] (NC4) | [COM SCAN OUTPUT MAP] (OSA)
NC5 | Com scan output 5 value | 16#31DD = 12765 | 16#2061/42 | 16#A0/01/A6 = 160/01/166 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out5 val.] (NC5) | [COM SCAN OUTPUT MAP] (OSA)
NC6 | Com scan output 6 value | 16#31DE = 12766 | 16#2061/43 | 16#A0/01/A7 = 160/01/167 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out6 val.] (NC6) | [COM SCAN OUTPUT MAP] (OSA)
NC7 | Com scan output 7 value | 16#31DF = 12767 | 16#2061/44 | 16#A0/01/A8 = 160/01/168 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out7 val.] (NC7) | [COM SCAN OUTPUT MAP] (OSA)
NC8 | Com scan output 8 value | 16#31E0 = 12768 | 16#2061/45 | 16#A0/01/A9 = 160/01/169 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out8 val.] (NC8) | [COM SCAN OUTPUT MAP] (OSA)
NM1 | Com scan input 1 value | 16#31C5 = 12741 | 16#2061/2A | 16#A0/01/8E = 160/01/142 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In1 val.] (NM1) | [COM. SCANNER INPUT MAP] (ISA)
NM2 | Com scan input 2 value | 16#31C6 = 12742 | 16#2061/2B | 16#A0/01/8F = 160/01/143 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In2 val.] (NM2) | [COM. SCANNER INPUT MAP] (ISA)
NM3 | Com scan input 3 value | 16#31C7 = 12743 | 16#2061/2C | 16#A0/01/90 = 160/01/144 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In3 val.] (NM3) | [COM. SCANNER INPUT MAP] (ISA)
NM4 | Com scan input 4 value | 16#31C8 = 12744 | 16#2061/2D | 16#A0/01/91 = 160/01/145 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In4 val.] (NM4) | [COM. SCANNER INPUT MAP] (ISA)
NM5 | Com scan input 5 value | 16#31C9 = 12745 | 16#2061/2E | 16#A0/01/92 = 160/01/146 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In5 val.] (NM5) | [COM. SCANNER INPUT MAP] (ISA)
NM6 | Com scan input 6 value | 16#31CA = 12746 | 16#2061/2F | 16#A0/01/93 = 160/01/147 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In6 val.] (NM6) | [COM. SCANNER INPUT MAP] (ISA)
NM7 | Com scan input 7 value | 16#31CB = 12747 | 16#2061/30 | 16#A0/01/94 = 160/01/148 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In7 val.] (NM7) | [COM. SCANNER INPUT MAP] (ISA)
NM8 | Com scan input 8 value | 16#31CC = 12748 | 16#2061/31 | 16#A0/01/95 = 160/01/149 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In8 val.] (NM8) | [COM. SCANNER INPUT MAP] (ISA)
SMAL | Velocity min amount | 16#21A1 = 8609 | 16#2038/A | 16#8C/01/0A = 140/01/10 |  | CiA 402 settings | R/W | UINT (Unsigned16) | 1 rpm |  | 0 rpm ... 65535 rpm
SMIL | Velocity max amount | 16#219F = 8607 | 16#2038/8 | 16#8C/01/08 = 140/01/08 |  | CiA 402 settings | R/W | UINT (Unsigned16) | 1 rpm |  | 0 rpm ... 65535 rpm
SPAL | Acceleration delta speed | 16#21A3 = 8611 | 16#2038/C | 16#8C/01/0C = 140/01/12 |  | CiA 402 settings | R/W | UINT (Unsigned16) | 1 rpm |  | 1 rpm ... 65535 rpm
SPAT | Acceleration delta time | 16#21A5 = 8613 | 16#2038/E | 16#8C/01/0E = 140/01/14 |  | CiA 402 settings | R/W | UINT (Unsigned16) | 1 s |  | 0 s ... 65535 s
SPDL | Deceleration delta speed | 16#21A6 = 8614 | 16#2038/F | 16#8C/01/0F = 140/01/15 |  | CiA 402 settings | R/W | UINT (Unsigned16) | 1 rpm |  | 1 rpm ... 65535 rpm
SPFN | Setpoint factor numerator | 16#21C2 = 8642 | 16#2038/2B | 16#8C/01/2B = 140/01/43 |  | CiA 402 settings | R/WS | UINT (Unsigned16) | 1 | 1 | 1 ... 65535
SPFD | Setpoint factor denominator | 16#21C3 = 8643 | 16#2038/2C | 16#8C/01/2C = 140/01/44 |  | CiA 402 settings | R/WS | UINT (Unsigned16) | 1 | 1 | 1 ... 65535
DOTD | Dis. operation opt code | 16#21CC = 8652 | 16#2038/35 | 16#8C/01/35 = 140/01/53 | DOTD | CiA 402 settings | R/WS | WORD (Enumeration) | - | [Ramp stop on fault] RMP |  | [Dis. operat opt code] (DOTD) | [STOP CONFIGURATION] (STT)
QSTD | Quick stop option code | 16#21CB = 8651 | 16#2038/34 | 16#8C/01/34 = 140/01/52 | QSTD | CiA 402 settings | R/WS | WORD (Enumeration) | - | [None] FST6
SCS | Save configuration | 16#1F41 = 8001 | 16#2032/2 | 16#89/01/02 = 137/01/02 | SCS | Configuration management | R/WS | WORD (Enumeration) | - | [No] NO
FCS | Restore configuration | 16#1F42 = 8002 | 16#2032/3 | 16#89/01/03 = 137/01/03 | FCS | Configuration management | R/WS | WORD (Enumeration) | - | [No] NO
FRY | Factory setting group | 16#0BCE = 3022 | 16#2000/17 | 16#70/01/17 = 112/01/23 |  | Configuration management | R/WS | WORD (BitString16) | - | BIT1
CHA1 | Parameter set sel 1 | 16#3266 = 12902 | 16#2063/3 | 16#A1/01/67 = 161/01/103 | PSLIN | Parameter set switching | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [2 Parameter sets] (CHA1) | [PARAM. SET SWITCHING] (MLP)
CHA2 | Parameter set sel 2 | 16#3267 = 12903 | 16#2063/4 | 16#A1/01/68 = 161/01/104 | PSLIN | Parameter set switching | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [3 Parameter sets] (CHA2) | [PARAM. SET SWITCHING] (MLP)
CFPS | Used parameter set | 16#3264 = 12900 | 16#2063/1 | 16#A1/01/65 = 161/01/101 | CFPS | Parameter set switching | R | WORD (Enumeration) | - |  |  | [Utilised param. set] (CFPS) | [MONITORING] (MON)
VAL | Load parameter set command | 16#3265 = 12901 | 16#2063/2 | 16#A1/01/66 = 161/01/102 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 1
AD01 | Parameter set address 1 | 16#326F = 12911 | 16#2063/C | 16#A1/01/70 = 161/01/112 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD02 | Parameter set address 2 | 16#3270 = 12912 | 16#2063/D | 16#A1/01/71 = 161/01/113 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD03 | Parameter set address 3 | 16#3271 = 12913 | 16#2063/E | 16#A1/01/72 = 161/01/114 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD04 | Parameter set address 4 | 16#3272 = 12914 | 16#2063/F | 16#A1/01/73 = 161/01/115 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD05 | Parameter set address 5 | 16#3273 = 12915 | 16#2063/10 | 16#A1/01/74 = 161/01/116 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD06 | Parameter set address 6 | 16#3274 = 12916 | 16#2063/11 | 16#A1/01/75 = 161/01/117 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD07 | Parameter set address 7 | 16#3275 = 12917 | 16#2063/12 | 16#A1/01/76 = 161/01/118 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD08 | Parameter set address 8 | 16#3276 = 12918 | 16#2063/13 | 16#A1/01/77 = 161/01/119 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD09 | Parameter set address 9 | 16#3277 = 12919 | 16#2063/14 | 16#A1/01/78 = 161/01/120 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD10 | Parameter set address 10 | 16#3278 = 12920 | 16#2063/15 | 16#A1/01/79 = 161/01/121 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD11 | Parameter set address 11 | 16#3279 = 12921 | 16#2063/16 | 16#A1/01/7A = 161/01/122 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD12 | Parameter set address 12 | 16#327A = 12922 | 16#2063/17 | 16#A1/01/7B = 161/01/123 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD13 | Parameter set address 13 | 16#327B = 12923 | 16#2063/18 | 16#A1/01/7C = 161/01/124 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD14 | Parameter set address 14 | 16#327C = 12924 | 16#2063/19 | 16#A1/01/7D = 161/01/125 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD15 | Parameter set address 15 | 16#327D = 12925 | 16#2063/1A | 16#A1/01/7E = 161/01/126 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
S101 | Parameter set 1 value 1 | 16#3283 = 12931 | 16#2063/20 | 16#A1/01/84 = 161/01/132 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S101) | [SET 1] (PS1)
S102 | Parameter set 1 value 2 | 16#3284 = 12932 | 16#2063/21 | 16#A1/01/85 = 161/01/133 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S102) | [SET 1] (PS1)
S103 | Parameter set 1 value 3 | 16#3285 = 12933 | 16#2063/22 | 16#A1/01/86 = 161/01/134 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S103) | [SET 1] (PS1)
S104 | Parameter set 1 value 4 | 16#3286 = 12934 | 16#2063/23 | 16#A1/01/87 = 161/01/135 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S104) | [SET 1] (PS1)
S105 | Parameter set 1 value 5 | 16#3287 = 12935 | 16#2063/24 | 16#A1/01/88 = 161/01/136 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S105) | [SET 1] (PS1)
S106 | Parameter set 1 value 6 | 16#3288 = 12936 | 16#2063/25 | 16#A1/01/89 = 161/01/137 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S106) | [SET 1] (PS1)
S107 | Parameter set 1 value 7 | 16#3289 = 12937 | 16#2063/26 | 16#A1/01/8A = 161/01/138 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S107) | [SET 1] (PS1)
S108 | Parameter set 1 value 8 | 16#328A = 12938 | 16#2063/27 | 16#A1/01/8B = 161/01/139 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S108) | [SET 1] (PS1)
S109 | Parameter set 1 value 9 | 16#328B = 12939 | 16#2063/28 | 16#A1/01/8C = 161/01/140 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S109) | [SET 1] (PS1)
S110 | Parameter set 1 value 10 | 16#328C = 12940 | 16#2063/29 | 16#A1/01/8D = 161/01/141 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S110) | [SET 1] (PS1)
S111 | Parameter set 1 value 11 | 16#328D = 12941 | 16#2063/2A | 16#A1/01/8E = 161/01/142 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S111) | [SET 1] (PS1)
S112 | Parameter set 1 value 12 | 16#328E = 12942 | 16#2063/2B | 16#A1/01/8F = 161/01/143 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S112) | [SET 1] (PS1)
S113 | Parameter set 1 value 13 | 16#328F = 12943 | 16#2063/2C | 16#A1/01/90 = 161/01/144 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S113) | [SET 1] (PS1)
S114 | Parameter set 1 value 14 | 16#3290 = 12944 | 16#2063/2D | 16#A1/01/91 = 161/01/145 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S114) | [SET 1] (PS1)
S115 | Parameter set 1 value 15 | 16#3291 = 12945 | 16#2063/2E | 16#A1/01/92 = 161/01/146 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S115) | [SET 1] (PS1)
S201 | Parameter set 2 value 1 | 16#3297 = 12951 | 16#2063/34 | 16#A1/01/98 = 161/01/152 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S201) | [SET 2] (PS2)
S202 | Parameter set 2 value 2 | 16#3298 = 12952 | 16#2063/35 | 16#A1/01/99 = 161/01/153 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S202) | [SET 2] (PS2)
S203 | Parameter set 2 value 3 | 16#3299 = 12953 | 16#2063/36 | 16#A1/01/9A = 161/01/154 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S203) | [SET 2] (PS2)
S204 | Parameter set 2 value 4 | 16#329A = 12954 | 16#2063/37 | 16#A1/01/9B = 161/01/155 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S204) | [SET 2] (PS2)
S205 | Parameter set 2 value 5 | 16#329B = 12955 | 16#2063/38 | 16#A1/01/9C = 161/01/156 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S205) | [SET 2] (PS2)
S206 | Parameter set 2 value 6 | 16#329C = 12956 | 16#2063/39 | 16#A1/01/9D = 161/01/157 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S206) | [SET 2] (PS2)
S207 | Parameter set 2 value 7 | 16#329D = 12957 | 16#2063/3A | 16#A1/01/9E = 161/01/158 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S207) | [SET 2] (PS2)
S208 | Parameter set 2 value 8 | 16#329E = 12958 | 16#2063/3B | 16#A1/01/9F = 161/01/159 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S208) | [SET 2] (PS2)
S209 | Parameter set 2 value 9 | 16#329F = 12959 | 16#2063/3C | 16#A1/01/A0 = 161/01/160 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S209) | [SET 2] (PS2)
S210 | Parameter set 2 value 10 | 16#32A0 = 12960 | 16#2063/3D | 16#A1/01/A1 = 161/01/161 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S210) | [SET 2] (PS2)
S211 | Parameter set 2 value 11 | 16#32A1 = 12961 | 16#2063/3E | 16#A1/01/A2 = 161/01/162 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S211) | [SET 2] (PS2)
S212 | Parameter set 2 value 12 | 16#32A2 = 12962 | 16#2063/3F | 16#A1/01/A3 = 161/01/163 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S212) | [SET 2] (PS2)
S213 | Parameter set 2 value 13 | 16#32A3 = 12963 | 16#2063/40 | 16#A1/01/A4 = 161/01/164 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S213) | [SET 2] (PS2)
S214 | Parameter set 2 value 14 | 16#32A4 = 12964 | 16#2063/41 | 16#A1/01/A5 = 161/01/165 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S214) | [SET 2] (PS2)
S215 | Parameter set 2 value 15 | 16#32A5 = 12965 | 16#2063/42 | 16#A1/01/A6 = 161/01/166 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S215) | [SET 2] (PS2)
S301 | Parameter set 3 value 1 | 16#32AB = 12971 | 16#2063/48 | 16#A1/01/AC = 161/01/172 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S301) | [SET 3] (PS3)
S302 | Parameter set 3 value 2 | 16#32AC = 12972 | 16#2063/49 | 16#A1/01/AD = 161/01/173 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S302) | [SET 3] (PS3)
S303 | Parameter set 3 value 3 | 16#32AD = 12973 | 16#2063/4A | 16#A1/01/AE = 161/01/174 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S303) | [SET 3] (PS3)
S304 | Parameter set 3 value 4 | 16#32AE = 12974 | 16#2063/4B | 16#A1/01/AF = 161/01/175 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S304) | [SET 3] (PS3)
S305 | Parameter set 3 value 5 | 16#32AF = 12975 | 16#2063/4C | 16#A1/01/B0 = 161/01/176 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S305) | [SET 3] (PS3)
S306 | Parameter set 3 value 6 | 16#32B0 = 12976 | 16#2063/4D | 16#A1/01/B1 = 161/01/177 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S306) | [SET 3] (PS3)
S307 | Parameter set 3 value 7 | 16#32B1 = 12977 | 16#2063/4E | 16#A1/01/B2 = 161/01/178 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S307) | [SET 3] (PS3)
S308 | Parameter set 3 value 8 | 16#32B2 = 12978 | 16#2063/4F | 16#A1/01/B3 = 161/01/179 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S308) | [SET 3] (PS3)
S309 | Parameter set 3 value 9 | 16#32B3 = 12979 | 16#2063/50 | 16#A1/01/B4 = 161/01/180 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S309) | [SET 3] (PS3)
S310 | Parameter set 3 value 10 | 16#32B4 = 12980 | 16#2063/51 | 16#A1/01/B5 = 161/01/181 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S310) | [SET 3] (PS3)
S311 | Parameter set 3 value 11 | 16#32B5 = 12981 | 16#2063/52 | 16#A1/01/B6 = 161/01/182 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S311) | [SET 3] (PS3)
S312 | Parameter set 3 value 12 | 16#32B6 = 12982 | 16#2063/53 | 16#A1/01/B7 = 161/01/183 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S312) | [SET 3] (PS3)
S313 | Parameter set 3 value 13 | 16#32B7 = 12983 | 16#2063/54 | 16#A1/01/B8 = 161/01/184 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S313) | [SET 3] (PS3)
S314 | Parameter set 3 value 14 | 16#32B8 = 12984 | 16#2063/55 | 16#A1/01/B9 = 161/01/185 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S314) | [SET 3] (PS3)
S315 | Parameter set 3 value 15 | 16#32B9 = 12985 | 16#2063/56 | 16#A1/01/BA = 161/01/186 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (S315) | [SET 3] (PS3)
LSP | Low speed | 16#0C21 = 3105 | 16#2001/6 | 16#70/01/6A = 112/01/106 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 599.0 Hz | [Low speed] (LSP) | [SIMPLY START] (SIM) [SETTINGS] (SET)
HSP | High Speed | 16#0C20 = 3104 | 16#2001/5 | 16#70/01/69 = 112/01/105 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 599.0 Hz | [High speed] (HSP) | [SIMPLY START] (SIM) [SETTINGS] (SET) [HSP SWITCHING] (CHS)
HSP2 | High speed 2 | 16#3B06 = 15110 | 16#2079/B | 16#AC/01/6F = 172/01/111 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 599.0 Hz | [High speed 2] (HSP2) | [SETTINGS] (SET) [HSP SWITCHING] (CHS)
HSP3 | High speed 3 | 16#3B07 = 15111 | 16#2079/C | 16#AC/01/70 = 172/01/112 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 599.0 Hz | [High speed 3] (HSP3) | [SETTINGS] (SET) [HSP SWITCHING] (CHS)
HSP4 | High speed 4 | 16#3B08 = 15112 | 16#2079/D | 16#AC/01/71 = 172/01/113 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 599.0 Hz | [High speed 4] (HSP4) | [SETTINGS] (SET) [HSP SWITCHING] (CHS)
SH2 | 2 High speed assign. | 16#3AFD = 15101 | 16#2079/2 | 16#AC/01/66 = 172/01/102 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [2 High speed] (SH2) | [HSP SWITCHING] (CHS)
SH4 | 4 High speed assign. | 16#3AFE = 15102 | 16#2079/3 | 16#AC/01/67 = 172/01/103 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [4 High speed] (SH4) | [HSP SWITCHING] (CHS)
ITH | Motor thermal current | 16#2596 = 9622 | 16#2042/17 | 16#91/01/17 = 145/01/23 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | Refer to programming manual | 0.0 A ... 6553.5 A | [Mot. therm. current] (ITH) | [SIMPLY START] (SIM) [SETTINGS] (SET)
SPGU | Inertia factor UF law | 16#259D = 9629 | 16#2042/1E | 16#91/01/1E = 145/01/30 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 40 % | 0 % ... 1000 % | [UF inertia comp.] (SPGU) | [SETTINGS] (SET) [MOTOR CONTROL] (DRC)
SPG | Speed proportional gain | 16#238F = 9103 | 16#203D/4 | 16#8E/01/68 = 142/01/104 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 40 % | 0 % ... 1000 % | [Speed prop. gain] (SPG) | [SETTINGS] (SET) [MOTOR CONTROL] (DRC)
SIT | Speed time integral | 16#2390 = 9104 | 16#203D/5 | 16#8E/01/69 = 142/01/105 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 63 ms | 1 ms ... 65535 ms | [Speed time integral] (SIT) | [SETTINGS] (SET) [MOTOR CONTROL] (DRC)
SFC | K speed loop filter | 16#2391 = 9105 | 16#203D/6 | 16#8E/01/6A = 142/01/106 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 65 | 0 ... 100 | [K speed loop filter] (SFC) | [SETTINGS] (SET) [MOTOR CONTROL] (DRC)
FFH | Filter time of the estimated speed | 16#239B = 9115 | 16#203D/10 | 16#8E/01/74 = 142/01/116 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 ms | 6.4 ms | 0.0 ms ... 100.0 ms | [Spd est. filter time] (FFH) | [MOTOR CONTROL] (DRC)
CRTF | Filter time of the reference currents | 16#239C = 9116 | 16#203D/11 | 16#8E/01/75 = 142/01/117 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 ms | 3.2 ms | 0.0 ms ... 100.0 ms | [Cur. ref. filter time] (CRTF) | [MOTOR CONTROL] (DRC)
CTD | Motor current detection | 16#2AF9 = 11001 | 16#2050/2 | 16#98/01/02 = 152/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | Refer to programming manual | 0.0 A ... 6553.5 A | [Current threshold] (CTD) | [SETTINGS] (SET) [ALARMS SETTING] (ALS)
TTH | High torque threshold | 16#2B08 = 11016 | 16#2050/11 | 16#98/01/11 = 152/01/17 |  | Configuration and settings | R/W | INT (Signed16) | 1 % | 100 % | -300 % ... 300 % | [High torque thd.] (TTH) | [SETTINGS] (SET) [ALARMS SETTING] (ALS)
TTL | Low torque threshold | 16#2B07 = 11015 | 16#2050/10 | 16#98/01/10 = 152/01/16 |  | Configuration and settings | R/W | INT (Signed16) | 1 % | 50 % | -300 % ... 300 % | [Low torque thd.] (TTL) | [SETTINGS] (SET) [ALARMS SETTING] (ALS)
FQL | Pulse warning threshold | 16#3911 = 14609 | 16#2074/A | 16#AA/01/0A = 170/01/10 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 Hz | 0 Hz | 0 Hz ... 20000 Hz | [Pulse warning thd.] (FQL) | [SETTINGS] (SET) [ALARMS SETTING] (ALS)
FTD | Motor freq. threshold | 16#2AFB = 11003 | 16#2050/4 | 16#98/01/04 = 152/01/04 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 599.0 Hz | [Freq. threshold] (FTD) | [SETTINGS] (SET) [ALARMS SETTING] (ALS)
F2D | Frequency threshold 2 | 16#2AFC = 11004 | 16#2050/5 | 16#98/01/05 = 152/01/05 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 599.0 Hz | [Freq. threshold 2] (F2D) | [SETTINGS] (SET) [ALARMS SETTING] (ALS)
JF2 | Skip frequency 2 | 16#2C26 = 11302 | 16#2053/3 | 16#99/01/67 = 153/01/103 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Skip Frequency 2] (JF2) | [SETTINGS] (SET) [PRESET SPEEDS] (PSS)
JPF | Skip frequency | 16#2C25 = 11301 | 16#2053/2 | 16#99/01/66 = 153/01/102 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Skip Frequency] (JPF) | [SETTINGS] (SET) [PRESET SPEEDS] (PSS)
JFH | Skip Freq. Hysteresis | 16#2C2F = 11311 | 16#2053/C | 16#99/01/70 = 153/01/112 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 1.0 Hz | 0.1 Hz ... 10.0 Hz | [Skip.Freq.Hysteresis] (JFH) | [SETTINGS] (SET) [PRESET SPEEDS] (PSS)
JF3 | 3rd Skip Frequency | 16#2C27 = 11303 | 16#2053/4 | 16#99/01/68 = 153/01/104 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [3rd Skip Frequency] (JF3) | [SETTINGS] (SET) [PRESET SPEEDS] (PSS)
BFR | Std. motor frequency | 16#0BC7 = 3015 | 16#2000/10 | 16#70/01/10 = 112/01/16 | BFR | Configuration and settings | R/WS | WORD (Enumeration) | - | [50Hz Motor frequency] 50Hz |  | [Standard mot. freq] (BFR) | [SIMPLY START] (SIM) [MOTOR CONTROL] (DRC)
NPR | Rated motor power | 16#258D = 9613 | 16#2042/E | 16#91/01/0E = 145/01/14 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [Rated motor power] (NPR) | [SIMPLY START] (SIM) [ASYNC. MOTOR] (ASY)
COS | Motor 1 Cosine Phi | 16#2586 = 9606 | 16#2042/7 | 16#91/01/07 = 145/01/07 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 | Refer to programming manual | 0.50 ... 1.00 | [Motor 1 Cosine Phi] (COS) | [ASYNC. MOTOR] (ASY)
UNS | Nominal motor voltage | 16#2581 = 9601 | 16#2042/2 | 16#91/01/02 = 145/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | Refer to programming manual | 100 V ... 690 V | [Rated motor volt.] (UNS) | [SIMPLY START] (SIM) [ASYNC. MOTOR] (ASY)
NCR | Nominal motor current | 16#2583 = 9603 | 16#2042/4 | 16#91/01/04 = 145/01/04 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 A | Refer to programming manual | 0.0 A ... 6553.5 A | [Rated mot. current] (NCR) | [SIMPLY START] (SIM) [ASYNC. MOTOR] (ASY)
FRS | Nominal motor frequency | 16#2582 = 9602 | 16#2042/3 | 16#91/01/03 = 145/01/03 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 10.0 Hz ... 800.0 Hz | [Rated motor freq.] (FRS) | [SIMPLY START] (SIM) [ASYNC. MOTOR] (ASY)
NSP | Nominal motor speed | 16#2584 = 9604 | 16#2042/5 | 16#91/01/05 = 145/01/05 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 rpm | Refer to programming manual | 0 rpm ... 65535 rpm | [Rated motor speed] (NSP) | [SIMPLY START] (SIM) [ASYNC. MOTOR] (ASY)
TFR | Max. output frequency | 16#0C1F = 3103 | 16#2001/4 | 16#70/01/68 = 112/01/104 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 10.0 Hz ... 599.0 Hz | [Max frequency] (TFR) | [SIMPLY START] (SIM) [MOTOR CONTROL] (DRC)
TUN | Automatic tuning | 16#2588 = 9608 | 16#2042/9 | 16#91/01/09 = 145/01/09 | ACTION | Configuration and settings | R/W | WORD (Enumeration) | - | [No action] NO |  | [Auto tuning] (TUN) | [SIMPLY START] (SIM) [ASYNC. MOTOR] (ASY) [SYNCHRONOUS MOTOR] (SYN)
AUT | Automatic autotune | 16#258F = 9615 | 16#2042/10 | 16#91/01/10 = 145/01/16 | AUT | Configuration and settings | R/W | WORD (Enumeration) | - | [No] NO |  | [Automatic autotune] (AUT) | [ASYNC. MOTOR] (ASY) [SYNCHRONOUS MOTOR] (SYN)
TUS | Auto-tuning state | 16#2589 = 9609 | 16#2042/A | 16#91/01/0A = 145/01/10 | ACT | Configuration and settings | R | WORD (Enumeration) | - | [Default stator resistance] TAB |  | [Auto tuning state] (TUS) | [SIMPLY START] (SIM) [ASYNC. MOTOR] (ASY) [SYNCHRONOUS MOTOR] (SYN)
CTT | Motor control type | 16#2587 = 9607 | 16#2042/8 | 16#91/01/08 = 145/01/08 | CTT | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Motor control type] (CTT) | [MOTOR CONTROL] (DRC)
U1 | Volt point 1 on 5pt V/F | 16#3073 = 12403 | 16#205E/4 | 16#9F/01/04 = 159/01/04 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 800 V | [U1] (U1) | [MOTOR CONTROL] (DRC)
F1 | Freq point 1on 5pt V/F | 16#3074 = 12404 | 16#205E/5 | 16#9F/01/05 = 159/01/05 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [F1] (F1) | [MOTOR CONTROL] (DRC)
U2 | Volt point 2 on 5pt V/F | 16#3075 = 12405 | 16#205E/6 | 16#9F/01/06 = 159/01/06 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 800 V | [U2] (U2) | [MOTOR CONTROL] (DRC)
F2 | Freq point 2 on 5pt V/F | 16#3076 = 12406 | 16#205E/7 | 16#9F/01/07 = 159/01/07 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [F2] (F2) | [MOTOR CONTROL] (DRC)
U3 | Volt point 3 on 5pt V/F | 16#3077 = 12407 | 16#205E/8 | 16#9F/01/08 = 159/01/08 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 800 V | [U3] (U3) | [MOTOR CONTROL] (DRC)
F3 | Freq point 3 on 5pt V/F | 16#3078 = 12408 | 16#205E/9 | 16#9F/01/09 = 159/01/09 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [F3] (F3) | [MOTOR CONTROL] (DRC)
U4 | Volt point 4 on 5pt V/F | 16#3079 = 12409 | 16#205E/A | 16#9F/01/0A = 159/01/10 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 800 V | [U4] (U4) | [MOTOR CONTROL] (DRC)
F4 | Freq point 4 on 5pt V/F | 16#307A = 12410 | 16#205E/B | 16#9F/01/0B = 159/01/11 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [F4] (F4) | [MOTOR CONTROL] (DRC)
U5 | Volt point 5 on 5pt V/F | 16#307B = 12411 | 16#205E/C | 16#9F/01/0C = 159/01/12 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 800 V | [U5] (U5) | [MOTOR CONTROL] (DRC)
F5 | Freq point 5 on 5pt V/F | 16#307C = 12412 | 16#205E/D | 16#9F/01/0D = 159/01/13 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [F5] (F5) | [MOTOR CONTROL] (DRC)
NCRS | Nominal sync current | 16#25C6 = 9670 | 16#2042/47 | 16#91/01/47 = 145/01/71 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 A | Refer to programming manual | 0.0 A ... 6553.5 A | [Nominal I sync.] (NCRS) | [SYNCHRONOUS MOTOR] (SYN)
NSPS | Nominal sync mot speed | 16#25C7 = 9671 | 16#2042/48 | 16#91/01/48 = 145/01/72 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 rpm | Refer to programming manual | 0 rpm ... 65535 rpm | [Nom motor spdsync] (NSPS) | [SYNCHRONOUS MOTOR] (SYN)
PPNS | Pole pairs number (sync) | 16#25C8 = 9672 | 16#2042/49 | 16#91/01/49 = 145/01/73 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | Refer to programming manual | 1 ... 50 | [Pole pairs] (PPNS) | [SYNCHRONOUS MOTOR] (SYN)
TQS | Motor torque | 16#25D4 = 9684 | 16#2042/55 | 16#91/01/55 = 145/01/85 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Nm | Refer to programming manual | 0.1 Nm ... 6553.5 Nm | [Motor torque] (TQS) | [SYNCHRONOUS MOTOR] (SYN)
PHS | Sync. EMF constant | 16#25C9 = 9673 | 16#2042/4A | 16#91/01/4A = 145/01/74 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mV/rpm | 0.0 mV/rpm | 0.0 mV/rpm ... 6553.5 mV/rpm | [Syn. EMF constant] (PHS) | [SYNCHRONOUS MOTOR] (SYN)
LDS | Sync motor d inductance | 16#25CA = 9674 | 16#2042/4B | 16#91/01/4B = 145/01/75 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 mH | 0.00 mH | 0.00 mH ... 655.35 mH | [Autotune L d-axis] (LDS) | [SYNCHRONOUS MOTOR] (SYN)
LQS | Sync motor q inductance | 16#25CB = 9675 | 16#2042/4C | 16#91/01/4C = 145/01/76 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 mH | 0.00 mH | 0.00 mH ... 655.35 mH | [Autotune L q-axis] (LQS) | [SYNCHRONOUS MOTOR] (SYN)
RSAS | Cust. stator resist. (sync) | 16#25D2 = 9682 | 16#2042/53 | 16#91/01/53 = 145/01/83 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 mOhm | 0 mOhm | 0 mOhm ... 65535 mOhm | [Cust. stator R syn] (RSAS) | [SYNCHRONOUS MOTOR] (SYN)
UFR | IR compensation | 16#2597 = 9623 | 16#2042/18 | 16#91/01/18 = 145/01/24 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 200 % | [IR compensation] (UFR) | [SETTINGS] (SET) [MOTOR CONTROL] (DRC)
SLP | Slip Compensation | 16#2599 = 9625 | 16#2042/1A | 16#91/01/1A = 145/01/26 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | Refer to programming manual | 0 % ... 300 % | [Slip compensation] (SLP) | [SETTINGS] (SET) [MOTOR CONTROL] (DRC)
PPN | Number of pairs of poles calculated | 16#2592 = 9618 | 16#2042/13 | 16#91/01/13 = 145/01/19 |  | Configuration and settings | R | UINT (Unsigned16) | 1 | Refer to programming manual | 1 ... 100
RSA | Cust stator resistance | 16#25AA = 9642 | 16#2042/2B | 16#91/01/2B = 145/01/43 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 mOhm | 0 mOhm | 0 mOhm ... 65535 mOhm | [Cust stator resist.] (RSA) | [ASYNC. MOTOR] (ASY)
IDA | Cust adjust magn. current | 16#25B4 = 9652 | 16#2042/35 | 16#91/01/35 = 145/01/53 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 A | 0.0 A | 0.0 A ... 6553.5 A | [Idw] (IDA) | [ASYNC. MOTOR] (ASY)
LFA | Cust leakage inductance | 16#25BE = 9662 | 16#2042/3F | 16#91/01/3F = 145/01/63 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 mH | 0.00 mH | 0.00 mH ... 655.35 mH | [Lfw] (LFA) | [ASYNC. MOTOR] (ASY)
TRA | Custom rotor t constant | 16#25C3 = 9667 | 16#2042/44 | 16#91/01/44 = 145/01/68 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 65535 ms | [Cust. rotor t const.] (TRA) | [ASYNC. MOTOR] (ASY)
FRSS | Nominal sync. motor freq. | 16#25CF = 9679 | 16#2042/50 | 16#91/01/50 = 145/01/80 |  | Configuration and settings | R | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 10.0 Hz ... 800.0 Hz | [Nominal freq sync.] (FRSS) | [SYNCHRONOUS MOTOR] (SYN)
SFR | Drive switching freq. | 16#0C1E = 3102 | 16#2001/3 | 16#70/01/67 = 112/01/103 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 kHz | 4.0 kHz | 2.0 kHz ... 16.0 kHz | [Switching freq.] (SFR) | [SETTINGS] (SET) [MOTOR CONTROL] (DRC)
CLI | Internal current limit | 16#23F1 = 9201 | 16#203E/2 | 16#8F/01/02 = 143/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | Refer to programming manual | 0.0 A ... 6553.5 A | [Current Limitation] (CLI) | [SETTINGS] (SET) [MOTOR CONTROL] (DRC) [2nd CURRENT LIMIT.] (CLI)
SFT | Switch. freq type | 16#0C1D = 3101 | 16#2001/2 | 16#70/01/66 = 112/01/102 | SFT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Switch.frequency type 1] HF1 |  | [Switch. freq type] (SFT) | [MOTOR CONTROL] (DRC)
NRD | Motor noise reduction | 16#0C23 = 3107 | 16#2001/8 | 16#70/01/6C = 112/01/108 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Noise reduction] (NRD) | [MOTOR CONTROL] (DRC)
BOA | Boost activation | 16#3656 = 13910 | 16#206D/B | 16#A6/01/6F = 166/01/111 | BOA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Dynamic] DYNA |  | [Boost activation] (BOA) | [MOTOR CONTROL] (DRC)
SVL | Motor surge limitation | 16#3139 = 12601 | 16#2060/2 | 16#A0/01/02 = 160/01/02 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Motor surge limit.] (SVL) | [MOTOR CONTROL] (DRC)
SOP | Optimize limit - volt surge | 16#313A = 12602 | 16#2060/3 | 16#A0/01/03 = 160/01/03 | SOP | Configuration and settings | R/WS | WORD (Enumeration) | - | [10 µs] 10 |  | [Volt surge limit. opt] (SOP) | [MOTOR CONTROL] (DRC)
VBR | Braking level | 16#3715 = 14101 | 16#206F/2 | 16#A7/01/66 = 167/01/102 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 V | Refer to programming manual | 335 V ... 995 V | [Braking level] (VBR) | [MOTOR CONTROL] (DRC) [DC Bus] (DCC)
LBA | Load sharing | 16#37DD = 14301 | 16#2071/2 | 16#A8/01/66 = 168/01/102 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Load sharing] (LBA) | [MOTOR CONTROL] (DRC)
LBC | Load correction | 16#37DE = 14302 | 16#2071/3 | 16#A8/01/67 = 168/01/103 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Load correction] (LBC) | [SETTINGS] (SET) [MOTOR CONTROL] (DRC)
LBC1 | Correction min speed | 16#37DF = 14303 | 16#2071/4 | 16#A8/01/68 = 168/01/104 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 598.9 Hz | [Correction min spd] (LBC1) | [MOTOR CONTROL] (DRC)
LBC2 | Correction max speed | 16#37E0 = 14304 | 16#2071/5 | 16#A8/01/69 = 168/01/105 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.1 Hz | 0.1 Hz ... 599.0 Hz | [Correction max spd] (LBC2) | [MOTOR CONTROL] (DRC)
LBC3 | Torque offset | 16#37E1 = 14305 | 16#2071/6 | 16#A8/01/6A = 168/01/106 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 300 % | [Torque offset] (LBC3) | [MOTOR CONTROL] (DRC)
LBF | Sharing filter | 16#37E2 = 14306 | 16#2071/7 | 16#A8/01/6B = 168/01/107 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 100 ms | 0 ms ... 20000 ms | [Sharing filter] (LBF) | [MOTOR CONTROL] (DRC)
FFM | Fan mode | 16#0C3A = 3130 | 16#2001/1F | 16#70/01/83 = 112/01/131 | FFM | Configuration and settings | R/W | WORD (Enumeration) | - | Refer to programming manual |  | [Fan mode] (FFM) | [SETTINGS] (SET)
TCC | 2 / 3 wire control | 16#2B5D = 11101 | 16#2051/2 | 16#98/01/66 = 152/01/102 | TCC | Configuration and settings | R/WS | WORD (Enumeration) | - | [2-wire control] 2C |  | [2/3 wire control] (TCC) | [SIMPLY START] (SIM) [INPUTS / OUTPUTS CFG] (I_O)
TCT | Type of 2 wire control | 16#2B5E = 11102 | 16#2051/3 | 16#98/01/67 = 152/01/103 | TCT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Edge triggered] TRN |  | [2 wire type] (TCT) | [INPUTS / OUTPUTS CFG] (I_O)
RRS | Reverse input assignment | 16#2B61 = 11105 | 16#2051/6 | 16#98/01/6A = 152/01/106 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Reverse assign.] (RRS) | [INPUTS / OUTPUTS CFG] (I_O)
BSP | Ref. template selection | 16#0C22 = 3106 | 16#2001/7 | 16#70/01/6B = 112/01/107 | BSP | Configuration and settings | R/W | WORD (Enumeration) | - | [Standard ref template] BSD |  | [Reference template] (BSP) | [INPUTS / OUTPUTS CFG] (I_O)
AI1T | Configuration of AI1 | 16#1132 = 4402 | 16#200E/3 | 16#77/01/03 = 119/01/03 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [AI in voltage selected] 10U |  | [AI1 Type] (AI1T) | [AI1 CONFIGURATION] (AI1)
UIL1 | AI1 minimum value | 16#113C = 4412 | 16#200E/D | 16#77/01/0D = 119/01/13 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AI1 min value] (UIL1) | [AI1] (AI1C) [AI1 CONFIGURATION] (AI1)
UIH1 | AI1 maximum value | 16#1146 = 4422 | 16#200E/17 | 16#77/01/17 = 119/01/23 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AI1 max value] (UIH1) | [AI1] (AI1C) [AI1 CONFIGURATION] (AI1)
AI1F | AI1 filter | 16#1164 = 4452 | 16#200E/35 | 16#77/01/35 = 119/01/53 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AI1 filter] (AI1F) | [AI1] (AI1C) [AI1 CONFIGURATION] (AI1)
AI1E | AI1 intermediate point X | 16#116E = 4462 | 16#200E/3F | 16#77/01/3F = 119/01/63 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI1 Interm. point X ] (AI1E) | [AI1 CONFIGURATION] (AI1)
AI1S | AI1 intermediate point Y | 16#1178 = 4472 | 16#200E/49 | 16#77/01/49 = 119/01/73 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI1 Interm. point Y] (AI1S) | [AI1 CONFIGURATION] (AI1)
AI2T | Configuration of AI2 | 16#1133 = 4403 | 16#200E/4 | 16#77/01/04 = 119/01/04 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [AI bipolar volts selected] N10U |  | [AI2 Type] (AI2T) | [AI2 CONFIGURATION] (AI2)
UIL2 | AI2 minimum value | 16#113D = 4413 | 16#200E/E | 16#77/01/0E = 119/01/14 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AI2 min value] (UIL2) | [AI2] (AI2C) [AI2 CONFIGURATION] (AI2)
UIH2 | AI2 maximum value | 16#1147 = 4423 | 16#200E/18 | 16#77/01/18 = 119/01/24 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AI2 max value] (UIH2) | [AI2] (AI2C) [AI2 CONFIGURATION] (AI2)
AI2F | AI2 filter | 16#1165 = 4453 | 16#200E/36 | 16#77/01/36 = 119/01/54 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AI2 filter] (AI2F) | [AI2] (AI2C) [AI2 CONFIGURATION] (AI2)
AI2E | AI2 intermediate point X | 16#116F = 4463 | 16#200E/40 | 16#77/01/40 = 119/01/64 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI2 Interm. point X] (AI2E) | [AI2 CONFIGURATION] (AI2)
AI2S | AI2 intermediate point Y | 16#1179 = 4473 | 16#200E/4A | 16#77/01/4A = 119/01/74 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI2 Interm. point Y] (AI2S) | [AI2 CONFIGURATION] (AI2)
AI3T | Configuration of AI3 | 16#1134 = 4404 | 16#200E/5 | 16#77/01/05 = 119/01/05 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [AI in current selected] 0A |  | [AI3 Type] (AI3T) | [AI3 CONFIGURATION] (AI3)
CRL3 | AI3 minimum value | 16#1152 = 4434 | 16#200E/23 | 16#77/01/23 = 119/01/35 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AI3 min. value] (CRL3) | [AI3] (AI3C) [AI3 CONFIGURATION] (AI3)
CRH3 | AI3 maximum value | 16#115C = 4444 | 16#200E/2D | 16#77/01/2D = 119/01/45 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AI3 max. value] (CRH3) | [AI3] (AI3C) [AI3 CONFIGURATION] (AI3)
AI3F | AI3 filter | 16#1166 = 4454 | 16#200E/37 | 16#77/01/37 = 119/01/55 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AI3 filter] (AI3F) | [AI3] (AI3C) [AI3 CONFIGURATION] (AI3)
AI3E | AI3 intermediate point X | 16#1170 = 4464 | 16#200E/41 | 16#77/01/41 = 119/01/65 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI3 Interm. point X] (AI3E) | [AI3 CONFIGURATION] (AI3)
AI3S | AI3 intermediate point Y | 16#117A = 4474 | 16#200E/4B | 16#77/01/4B = 119/01/75 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI3 Interm. point Y] (AI3S) | [AI3 CONFIGURATION] (AI3)
AO1 | AO1 assignment | 16#139D = 5021 | 16#2014/16 | 16#7A/01/16 = 122/01/22 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [AO1 assignment] (AO1) | [AO1] (AO1C) [AO1 CONFIGURATION] (AO1)
AO1T | Configuration of AO1 | 16#11F9 = 4601 | 16#2010/2 | 16#78/01/02 = 120/01/02 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [AI in current selected] 0A |  | [AO1 Type] (AO1T) | [AO1 CONFIGURATION] (AO1)
AOF1 | Enable AQ1 fallback | 16#10C5 = 4293 | 16#200C/5E | 16#76/01/5E = 118/01/94 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Enable AQ1 fallback] (AOF1) | [AO1 CONFIGURATION] (AO1)
AOL1 | AO1 min output value | 16#1221 = 4641 | 16#2010/2A | 16#78/01/2A = 120/01/42 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AO1 min output] (AOL1) | [AO1] (AO1C) [AO1 CONFIGURATION] (AO1)
AOH1 | AO1 max output value | 16#122B = 4651 | 16#2010/34 | 16#78/01/34 = 120/01/52 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AO1 max output] (AOH1) | [AO1] (AO1C) [AO1 CONFIGURATION] (AO1)
UOL1 | AO1 minimum output | 16#120D = 4621 | 16#2010/16 | 16#78/01/16 = 120/01/22 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AO1 min Output] (UOL1) | [AO1] (AO1C) [AO1 CONFIGURATION] (AO1)
UOH1 | AO1 maximum output | 16#1217 = 4631 | 16#2010/20 | 16#78/01/20 = 120/01/32 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AO1 max Output] (UOH1) | [AO1] (AO1C) [AO1 CONFIGURATION] (AO1)
ASL1 | Scaling AO1 min | 16#1235 = 4661 | 16#2010/3E | 16#78/01/3E = 120/01/62 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Scaling AO1 min] (ASL1) | [AO1] (AO1C) [AO1 CONFIGURATION] (AO1)
ASH1 | Scaling AO1 max | 16#123F = 4671 | 16#2010/48 | 16#78/01/48 = 120/01/72 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 % | 100.0 % | 0.0 % ... 100.0 % | [Scaling AO1 max] (ASH1) | [AO1] (AO1C) [AO1 CONFIGURATION] (AO1)
AO1F | AO1 filter | 16#1203 = 4611 | 16#2010/C | 16#78/01/0C = 120/01/12 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AO1 Filter] (AO1F) | [AO1] (AO1C) [AO1 CONFIGURATION] (AO1)
FR1 | Configuration reference 1 | 16#20DD = 8413 | 16#2036/E | 16#8B/01/0E = 139/01/14 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Ref.1 channel] (FR1) | [COMMAND] (CTL)
RIN | Reverse direction inhibit. | 16#0C24 = 3108 | 16#2001/9 | 16#70/01/6D = 112/01/109 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [RV Inhibition] (RIN) | [COMMAND] (CTL)
PST | STOP key priority | 16#FA02 = 64002 |  |  | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [Yes] YES |  | [Stop Key priority] (PST) | [COMMAND] (CTL)
CHCF | Channel mode config. | 16#20D1 = 8401 | 16#2036/2 | 16#8B/01/02 = 139/01/02 | CHCF | Configuration and settings | R/WS | WORD (Enumeration) | - | [Combined channel mode] SIM |  | [Profile] (CHCF) | [COMMAND] (CTL)
CCS | Cmd channel switch | 16#20E5 = 8421 | 16#2036/16 | 16#8B/01/16 = 139/01/22 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Control ch. = Channel 1] CD1 |  | [Cmd switching] (CCS) | [COMMAND] (CTL)
CD1 | Control channel 1 config. | 16#20E7 = 8423 | 16#2036/18 | 16#8B/01/18 = 139/01/24 | CDX | Configuration and settings | R/WS | WORD (Enumeration) | - | [Terminal block] TER |  | [Cmd channel 1] (CD1) | [COMMAND] (CTL)
CD2 | Control channel 2 config. | 16#20E8 = 8424 | 16#2036/19 | 16#8B/01/19 = 139/01/25 | CDX | Configuration and settings | R/WS | WORD (Enumeration) | - | [Modbus communication] MDB |  | [Cmd channel 2] (CD2) | [COMMAND] (CTL)
RFC | Select switching (1 to 2) | 16#20DB = 8411 | 16#2036/C | 16#8B/01/0C = 139/01/12 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Ref. 2 switching] (RFC) | [COMMAND] (CTL)
FR2 | Configuration reference 2 | 16#20DE = 8414 | 16#2036/F | 16#8B/01/0F = 139/01/15 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Ref.2 channel] (FR2) | [COMMAND] (CTL)
COP | Copy Ch.1 <-> Ch. 2 | 16#20D2 = 8402 | 16#2036/3 | 16#8B/01/03 = 139/01/03 | COP | Configuration and settings | R/WS | WORD (Enumeration) | - | [No copy] NO |  | [Copy channel 1<>2] (COP) | [COMMAND] (CTL)
FN1 | F1 key assignment | 16#34BD = 13501 | 16#2069/2 | 16#A4/01/66 = 164/01/102 | CSLFN | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [F1 key assignment] (FN1) | [COMMAND] (CTL)
FN2 | F2 key assignment | 16#34BE = 13502 | 16#2069/3 | 16#A4/01/67 = 164/01/103 | CSLFN | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [F2 key assignment] (FN2) | [COMMAND] (CTL)
FN3 | F3 key assignment | 16#34BF = 13503 | 16#2069/4 | 16#A4/01/68 = 164/01/104 | CSLFN | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [F3 key assignment] (FN3) | [COMMAND] (CTL)
FN4 | F4 key assignment | 16#34C0 = 13504 | 16#2069/5 | 16#A4/01/69 = 164/01/105 | CSLFN | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [F4 key assignment] (FN4) | [COMMAND] (CTL)
BMP | HMI command | 16#34D9 = 13529 | 16#2069/1E | 16#A4/01/82 = 164/01/130 | BMP | Configuration and settings | R/WS | WORD (Enumeration) | - | [Cmd/ref clear on c/over] STOP |  | [HMI cmd.] (BMP) | [COMMAND] (CTL)
RCB | Select switching (1 to 1B) | 16#20DC = 8412 | 16#2036/D | 16#8B/01/0D = 139/01/13 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Command ch = ch 1] FR1 |  | [Ref 1B switching] (RCB) | [REFERENCE SWITCH.] (REF)
FR1B | Configuration ref. 1B | 16#20DF = 8415 | 16#2036/10 | 16#8B/01/10 = 139/01/16 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Ref.1B channel] (FR1B) | [REFERENCE SWITCH.] (REF)
SA2 | Summing input 2 | 16#2E19 = 11801 | 16#2058/2 | 16#9C/01/02 = 156/01/02 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Summing ref. 2] (SA2) | [REF. OPERATIONS] (OAI)
SA3 | Summing input 3 | 16#2E1A = 11802 | 16#2058/3 | 16#9C/01/03 = 156/01/03 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Summing ref. 3] (SA3) | [REF. OPERATIONS] (OAI)
DA2 | Subtract reference 2 | 16#2E23 = 11811 | 16#2058/C | 16#9C/01/0C = 156/01/12 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Subtract ref. 2] (DA2) | [REF. OPERATIONS] (OAI)
DA3 | Subtract reference 3 | 16#2E24 = 11812 | 16#2058/D | 16#9C/01/0D = 156/01/13 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Subtract ref. 3] (DA3) | [REF. OPERATIONS] (OAI)
MA2 | Multiplier reference 2 | 16#2E2D = 11821 | 16#2058/16 | 16#9C/01/16 = 156/01/22 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Multiplier ref. 2] (MA2) | [REF. OPERATIONS] (OAI)
MA3 | Multiplier reference 3 | 16#2E2E = 11822 | 16#2058/17 | 16#9C/01/17 = 156/01/23 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Multiplier ref. 3] (MA3) | [REF. OPERATIONS] (OAI)
RPT | Type of reference ramp | 16#232C = 9004 | 16#203C/5 | 16#8E/01/05 = 142/01/05 | RPT | Configuration and settings | R/W | WORD (Enumeration) | - | [Linear ramp] LIN |  | [Ramp type] (RPT) | [RAMP] (RPT)
INR | Ramp increment | 16#233C = 9020 | 16#203C/15 | 16#8E/01/15 = 142/01/21 | INR | Configuration and settings | R/W | WORD (Enumeration) | - | [tenths of seconds] 01 |  | [Ramp increment] (INR) | [SETTINGS] (SET) [RAMP] (RPT)
ACC | Acceleration ramp time | 16#2329 = 9001 | 16#203C/2 | 16#8E/01/02 = 142/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 30 | 0 ... 9999 | [Acceleration] (ACC) | [SIMPLY START] (SIM) [SETTINGS] (SET) [RAMP] (RPT)
DEC | Deceleration ramp time | 16#232A = 9002 | 16#203C/3 | 16#8E/01/03 = 142/01/03 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 30 | 0 ... 9999 | [Deceleration] (DEC) | [SIMPLY START] (SIM) [SETTINGS] (SET) [RAMP] (RPT) [None] (TDC)
TA1 | Start ACC ramp rounding | 16#232D = 9005 | 16#203C/6 | 16#8E/01/06 = 142/01/06 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 100 % | [Begin Acc round] (TA1) | [SETTINGS] (SET) [RAMP] (RPT)
TA2 | End ACC ramp rounding | 16#232E = 9006 | 16#203C/7 | 16#8E/01/07 = 142/01/07 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 100 % | [End Acc round] (TA2) | [SETTINGS] (SET) [RAMP] (RPT)
TA3 | Start DEC ramp rounding | 16#232F = 9007 | 16#203C/8 | 16#8E/01/08 = 142/01/08 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 100 % | [Begin Dec round] (TA3) | [SETTINGS] (SET) [RAMP] (RPT)
TA4 | End DEC rounding coeff. | 16#2330 = 9008 | 16#203C/9 | 16#8E/01/09 = 142/01/09 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 100 % | [End Dec round] (TA4) | [SETTINGS] (SET) [RAMP] (RPT)
FRT | Ramp 2 freq. threshold | 16#2333 = 9011 | 16#203C/C | 16#8E/01/0C = 142/01/12 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Ramp 2 threshold] (FRT) | [RAMP] (RPT)
RPS | Ramp switching input | 16#2332 = 9010 | 16#203C/B | 16#8E/01/0B = 142/01/11 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Ramp switch ass.] (RPS) | [RAMP] (RPT)
AC2 | Acceleration 2 ramp time | 16#2334 = 9012 | 16#203C/D | 16#8E/01/0D = 142/01/13 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 50 | 1 ... 9999 | [Acceleration 2] (AC2) | [SETTINGS] (SET) [RAMP] (RPT) [+/-SPEED AROUND REF.] (SRE) [PID REGULATOR] (PID)
DE2 | Deceleration 2 ramp time | 16#2335 = 9013 | 16#203C/E | 16#8E/01/0E = 142/01/14 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 50 | 1 ... 9999 | [Deceleration 2] (DE2) | [SETTINGS] (SET) [RAMP] (RPT) [+/-SPEED AROUND REF.] (SRE)
BRA | Decel ramp adaptation | 16#232B = 9003 | 16#203C/4 | 16#8E/01/04 = 142/01/04 | BRA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Dec ramp adapt assigned] YES |  | [Dec ramp adapt.] (BRA) | [RAMP] (RPT)
STT | Normal stop mode | 16#2BC1 = 11201 | 16#2052/2 | 16#99/01/02 = 153/01/02 | STT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Stop on decel. ramp] RMP |  | [Type of stop] (STT) | [STOP CONFIGURATION] (STT)
FFT | Freewheel stop threshold | 16#2BD4 = 11220 | 16#2052/15 | 16#99/01/15 = 153/01/21 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.2 Hz ... 599.0 Hz | [Freewheel stop Thd] (FFT) | [SETTINGS] (SET) [STOP CONFIGURATION] (STT)
NST | Freewheel stop input | 16#2BC2 = 11202 | 16#2052/3 | 16#99/01/03 = 153/01/03 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Freewheel stop ass.] (NST) | [STOP CONFIGURATION] (STT)
FST | Fast stop input assign. | 16#2BC4 = 11204 | 16#2052/5 | 16#99/01/05 = 153/01/05 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Fast stop assign.] (FST) | [STOP CONFIGURATION] (STT)
DCF | Fast stop ramp coefficient | 16#2BDE = 11230 | 16#2052/1F | 16#99/01/1F = 153/01/31 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 4 | 0 ... 10 | [Ramp divider] (DCF) | [SETTINGS] (SET) [STOP CONFIGURATION] (STT) [RAMP DIVIDER] (FST)
DCI | DC brake via logic input | 16#2BC3 = 11203 | 16#2052/4 | 16#99/01/04 = 153/01/04 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [DC injection assign.] (DCI) | [STOP CONFIGURATION] (STT)
IDC | DC injection current 1 | 16#2BCA = 11210 | 16#2052/B | 16#99/01/0B = 153/01/11 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | Refer to programming manual | 0.0 A ... 6553.5 A | [DC inject. level 1] (IDC) | [SETTINGS] (SET) [STOP CONFIGURATION] (STT) [DC INJECTION] (DCI)
TDI | DC injection time 1 | 16#2BCD = 11213 | 16#2052/E | 16#99/01/0E = 153/01/14 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 30.0 s | [DC injection time 1] (TDI) | [SETTINGS] (SET) [STOP CONFIGURATION] (STT) [DC INJECTION] (DCI)
IDC2 | DC injection current 2 | 16#2BCC = 11212 | 16#2052/D | 16#99/01/0D = 153/01/13 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | Refer to programming manual | 0.0 A ... 6553.5 A | [DC inject. level 2] (IDC2) | [SETTINGS] (SET) [STOP CONFIGURATION] (STT) [DC INJECTION] (DCI)
TDC | DC injection time 2 | 16#2BCB = 11211 | 16#2052/C | 16#99/01/0C = 153/01/12 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 30.0 s | [DC injection time 2] (TDC) | [SETTINGS] (SET) [STOP CONFIGURATION] (STT) [DC INJECTION] (DCI)
ADC | Automatic DC injection | 16#28A1 = 10401 | 16#204A/2 | 16#95/01/02 = 149/01/02 | ADC | Configuration and settings | R/W | WORD (Enumeration) | - | Refer to programming manual |  | [Auto DC injection] (ADC) | [AUTO DC INJECTION] (ADC)
SDC1 | Auto DC injection level 1 | 16#28A3 = 10403 | 16#204A/4 | 16#95/01/04 = 149/01/04 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | Refer to programming manual | 0.0 A ... 6553.5 A | [Auto DC inj. level 1] (SDC1) | [SETTINGS] (SET) [AUTO DC INJECTION] (ADC) [BRAKE LOGIC CONTROL] (BLC)
TDC1 | Auto DC injection time 1 | 16#28A2 = 10402 | 16#204A/3 | 16#95/01/03 = 149/01/03 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 30.0 s | [Auto DC inj. time 1] (TDC1) | [SETTINGS] (SET) [AUTO DC INJECTION] (ADC)
SDC2 | Auto DC injection level 2 | 16#28A5 = 10405 | 16#204A/6 | 16#95/01/06 = 149/01/06 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | Refer to programming manual | 0.0 A ... 6553.5 A | [Auto DC inj. level 2] (SDC2) | [SETTINGS] (SET) [AUTO DC INJECTION] (ADC)
TDC2 | Auto DC injection time 2 | 16#28A4 = 10404 | 16#204A/5 | 16#95/01/05 = 149/01/05 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 30.0 s | [Auto DC inj. time 2] (TDC2) | [SETTINGS] (SET) [AUTO DC INJECTION] (ADC)
JOG | Jog assignment | 16#2B66 = 11110 | 16#2051/B | 16#98/01/6F = 152/01/111 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [JOG] (JOG) | [JOG] (JOG)
JGF | Jog frequency | 16#2B67 = 11111 | 16#2051/C | 16#98/01/70 = 152/01/112 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 10.0 Hz | 0.0 Hz ... 10.0 Hz | [Jog frequency] (JGF) | [SETTINGS] (SET) [JOG] (JOG)
JGT | Jog Delay | 16#2B68 = 11112 | 16#2051/D | 16#98/01/71 = 152/01/113 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.0 s ... 2.0 s | [Jog delay] (JGT) | [SETTINGS] (SET) [JOG] (JOG)
PS2 | 2 preset speeds assign. | 16#2C89 = 11401 | 16#2054/2 | 16#9A/01/02 = 154/01/02 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [2 preset speeds] (PS2) | [PRESET SPEEDS] (PSS)
PS4 | 4 preset speeds assign. | 16#2C8A = 11402 | 16#2054/3 | 16#9A/01/03 = 154/01/03 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [4 preset speeds] (PS4) | [PRESET SPEEDS] (PSS)
PS8 | 8 preset speeds assign. | 16#2C8B = 11403 | 16#2054/4 | 16#9A/01/04 = 154/01/04 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [8 preset speeds] (PS8) | [PRESET SPEEDS] (PSS)
PS16 | 16 preset speeds assign. | 16#2C8C = 11404 | 16#2054/5 | 16#9A/01/05 = 154/01/05 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [16 preset speeds] (PS16) | [PRESET SPEEDS] (PSS)
SP2 | Preset speed 2 | 16#2C92 = 11410 | 16#2054/B | 16#9A/01/0B = 154/01/11 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 10.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 2] (SP2) | [SETTINGS] (SET) [PRESET SPEEDS] (PSS)
SP3 | Preset speed 3 | 16#2C93 = 11411 | 16#2054/C | 16#9A/01/0C = 154/01/12 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 15.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 3] (SP3) | [SETTINGS] (SET) [PRESET SPEEDS] (PSS)
SP4 | Preset speed 4 | 16#2C94 = 11412 | 16#2054/D | 16#9A/01/0D = 154/01/13 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 20.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 4] (SP4) | [SETTINGS] (SET) [PRESET SPEEDS] (PSS)
SP5 | Preset speed 5 | 16#2C95 = 11413 | 16#2054/E | 16#9A/01/0E = 154/01/14 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 25.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 5] (SP5) | [SETTINGS] (SET) [PRESET SPEEDS] (PSS)
SP6 | Preset speed 6 | 16#2C96 = 11414 | 16#2054/F | 16#9A/01/0F = 154/01/15 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 30.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 6] (SP6) | [SETTINGS] (SET) [PRESET SPEEDS] (PSS)
SP7 | Preset speed 7 | 16#2C97 = 11415 | 16#2054/10 | 16#9A/01/10 = 154/01/16 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 35.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 7] (SP7) | [SETTINGS] (SET) [PRESET SPEEDS] (PSS)
SP8 | Preset speed 8 | 16#2C98 = 11416 | 16#2054/11 | 16#9A/01/11 = 154/01/17 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 40.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 8] (SP8) | [SETTINGS] (SET) [PRESET SPEEDS] (PSS)
SP9 | Preset speed 9 | 16#2C99 = 11417 | 16#2054/12 | 16#9A/01/12 = 154/01/18 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 45.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 9] (SP9) | [SETTINGS] (SET) [PRESET SPEEDS] (PSS)
SP10 | Preset speed 10 | 16#2C9A = 11418 | 16#2054/13 | 16#9A/01/13 = 154/01/19 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 50.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 10] (SP10) | [SETTINGS] (SET) [PRESET SPEEDS] (PSS)
SP11 | Preset speed 11 | 16#2C9B = 11419 | 16#2054/14 | 16#9A/01/14 = 154/01/20 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 55.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 11] (SP11) | [SETTINGS] (SET) [PRESET SPEEDS] (PSS)
SP12 | Preset speed 12 | 16#2C9C = 11420 | 16#2054/15 | 16#9A/01/15 = 154/01/21 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 60.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 12] (SP12) | [SETTINGS] (SET) [PRESET SPEEDS] (PSS)
SP13 | Preset speed 13 | 16#2C9D = 11421 | 16#2054/16 | 16#9A/01/16 = 154/01/22 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 70.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 13] (SP13) | [SETTINGS] (SET) [PRESET SPEEDS] (PSS)
SP14 | Preset speed 14 | 16#2C9E = 11422 | 16#2054/17 | 16#9A/01/17 = 154/01/23 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 80.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 14] (SP14) | [SETTINGS] (SET) [PRESET SPEEDS] (PSS)
SP15 | Preset speed 15 | 16#2C9F = 11423 | 16#2054/18 | 16#9A/01/18 = 154/01/24 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 90.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 15] (SP15) | [SETTINGS] (SET) [PRESET SPEEDS] (PSS)
SP16 | Preset speed 16 | 16#2CA0 = 11424 | 16#2054/19 | 16#9A/01/19 = 154/01/25 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 100.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 16] (SP16) | [SETTINGS] (SET) [PRESET SPEEDS] (PSS)
USP | Increase spd input assign | 16#2CED = 11501 | 16#2055/2 | 16#9A/01/66 = 154/01/102 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [+ speed assignment] (USP) | [+/- SPEED] (UPD)
DSP | Down spd input assign. | 16#2CEE = 11502 | 16#2055/3 | 16#9A/01/67 = 154/01/103 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [-Speed assignment] (DSP) | [+/- SPEED] (UPD)
STR | Freq. reference stored | 16#2CEF = 11503 | 16#2055/4 | 16#9A/01/68 = 154/01/104 | STR | Configuration and settings | R/WS | WORD (Enumeration) | - | [No save] NO |  | [Reference saved] (STR) | [+/- SPEED] (UPD)
USI | Increase spd input assign | 16#2D00 = 11520 | 16#2055/15 | 16#9A/01/79 = 154/01/121 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [+ speed assignment] (USI) | [+/-SPEED AROUND REF.] (SRE)
DSI | Down spd input assign. | 16#2D01 = 11521 | 16#2055/16 | 16#9A/01/7A = 154/01/122 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [-Speed assignment] (DSI) | [+/-SPEED AROUND REF.] (SRE)
SRP | +/-Speed limitation | 16#2CF1 = 11505 | 16#2055/6 | 16#9A/01/6A = 154/01/106 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 50 % | [+/-Speed limitation] (SRP) | [SETTINGS] (SET) [+/-SPEED AROUND REF.] (SRE)
SPM | Reference memory input | 16#212B = 8491 | 16#2036/5C | 16#8B/01/5C = 139/01/92 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Ref. memo ass.] (SPM) | [MEMO REFERENCE] (SPM)
FLU | Motor fluxing configure | 16#364E = 13902 | 16#206D/3 | 16#A6/01/67 = 166/01/103 | FLU | Configuration and settings | R/W | WORD (Enumeration) | - | [No Pre fluxing] FNO |  | [Motor fluxing] (FLU) | [SETTINGS] (SET) [ASYNC. MOTOR] (ASY) [FLUXING BY LI] (FLI)
FLI | Fluxing input assignment | 16#364D = 13901 | 16#206D/2 | 16#A6/01/66 = 166/01/102 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Fluxing assignment] (FLI) | [FLUXING BY LI] (FLI)
AST | Auto angle setting type | 16#3665 = 13925 | 16#206D/1A | 16#A6/01/7E = 166/01/126 | AST | Configuration and settings | R/WS | WORD (Enumeration) | - | [Pulse Signal Injection - Optimized] PSIO |  | [Angle setting type] (AST) | [SYNCHRONOUS MOTOR] (SYN) [FLUXING BY LI] (FLI)
HFI | Activation of HF injection | 16#3CF0 = 15600 | 16#207E/1 | 16#AF/01/01 = 175/01/01 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [HF inj. activation] (HFI) | [SYNCHRONOUS MOTOR] (SYN)
HIR | Current level of the HF injection signal | 16#3CF2 = 15602 | 16#207E/3 | 16#AF/01/03 = 175/01/03 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 25 % | 0 % ... 200 % | [HF current level] (HIR) | [SYNCHRONOUS MOTOR] (SYN)
SPB | Bandwidth of the HF PLL | 16#3CF3 = 15603 | 16#207E/4 | 16#AF/01/04 = 175/01/04 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 Hz | 25 Hz | 0 Hz ... 100 Hz | [HF pll bandwidth] (SPB) | [SYNCHRONOUS MOTOR] (SYN)
ILR | Current level of the HF alignment | 16#3CF5 = 15605 | 16#207E/6 | 16#AF/01/06 = 175/01/06 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 50 % | 0 % ... 200 % | [Injection level align.] (ILR) | [SYNCHRONOUS MOTOR] (SYN)
SIR | Boost level for IPMA alignment | 16#3CF6 = 15606 | 16#207E/7 | 16#AF/01/07 = 175/01/07 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 200 % | [Boost level align.] (SIR) | [SYNCHRONOUS MOTOR] (SYN)
MCR | Maximum current of PSI alignment | 16#3CF7 = 15607 | 16#207E/8 | 16#AF/01/08 = 175/01/08 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 300 % | [PSI align curr. max] (MCR) | [SYNCHRONOUS MOTOR] (SYN)
PEC | Angle position error compensation | 16#3CF8 = 15608 | 16#207E/9 | 16#AF/01/09 = 175/01/09 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 500 % | [Angle error Comp.] (PEC) | [SYNCHRONOUS MOTOR] (SYN)
BLC | Brake logic assignment | 16#2711 = 10001 | 16#2046/2 | 16#93/01/02 = 147/01/02 | BLC | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Brake assignment] (BLC) | [BRAKE LOGIC CONTROL] (BLC)
BST | Motion type selection | 16#2718 = 10008 | 16#2046/9 | 16#93/01/09 = 147/01/09 | BST | Configuration and settings | R/WS | WORD (Enumeration) | - | [Hoisting motion] VER |  | [Movement type] (BST) | [BRAKE LOGIC CONTROL] (BLC)
BCI | Brake contact input | 16#2719 = 10009 | 16#2046/A | 16#93/01/0A = 147/01/10 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Brake contact] (BCI) | [BRAKE LOGIC CONTROL] (BLC)
BIP | Brake release pulse | 16#2717 = 10007 | 16#2046/8 | 16#93/01/08 = 147/01/08 | BIP | Configuration and settings | R/W | WORD (Enumeration) | - | Refer to programming manual |  | [Brake impulse] (BIP) | [BRAKE LOGIC CONTROL] (BLC)
IBR | Brake release current | 16#2716 = 10006 | 16#2046/7 | 16#93/01/07 = 147/01/07 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | 0.0 A | 0.0 A ... 6553.5 A | [Brake release I FW] (IBR) | [SETTINGS] (SET) [BRAKE LOGIC CONTROL] (BLC)
IRD | Rev. brake release curr. | 16#271B = 10011 | 16#2046/C | 16#93/01/0C = 147/01/12 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | 0.0 A | 0.0 A ... 6553.5 A | [Brake release I Rev] (IRD) | [SETTINGS] (SET) [BRAKE LOGIC CONTROL] (BLC)
BRT | Brake release time | 16#2714 = 10004 | 16#2046/5 | 16#93/01/05 = 147/01/05 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 5.00 s | [Brake Release time] (BRT) | [SETTINGS] (SET) [BRAKE LOGIC CONTROL] (BLC)
BIR | Brake release frequency | 16#271C = 10012 | 16#2046/D | 16#93/01/0D = 147/01/13 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | Refer to programming manual | -0.1 Hz ... 10.0 Hz | [Brake release freq] (BIR) | [SETTINGS] (SET) [BRAKE LOGIC CONTROL] (BLC)
BEN | Brake engage frequency | 16#2713 = 10003 | 16#2046/4 | 16#93/01/04 = 147/01/04 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | -0.1 Hz | -0.1 Hz ... 10.0 Hz | [Brake engage freq] (BEN) | [SETTINGS] (SET) [BRAKE LOGIC CONTROL] (BLC)
TBE | Brake engage delay | 16#271A = 10010 | 16#2046/B | 16#93/01/0B = 147/01/11 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 5.00 s | [Brake engage delay] (TBE) | [SETTINGS] (SET) [BRAKE LOGIC CONTROL] (BLC)
BET | Brake engage time | 16#2715 = 10005 | 16#2046/6 | 16#93/01/06 = 147/01/06 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 5.00 s | [Brake engage time] (BET) | [SETTINGS] (SET) [BRAKE LOGIC CONTROL] (BLC)
BED | Brake engage at reversal | 16#2724 = 10020 | 16#2046/15 | 16#93/01/15 = 147/01/21 | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [No] NO |  | [Engage at reversal] (BED) | [BRAKE LOGIC CONTROL] (BLC)
JDC | Jump at reversal | 16#271D = 10013 | 16#2046/E | 16#93/01/0E = 147/01/14 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | Refer to programming manual | -0.1 Hz ... 10.0 Hz | [Jump at reversal] (JDC) | [SETTINGS] (SET) [BRAKE LOGIC CONTROL] (BLC)
TTR | Time to restart | 16#2726 = 10022 | 16#2046/17 | 16#93/01/17 = 147/01/23 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 15.00 s | [Time to restart] (TTR) | [SETTINGS] (SET) [BRAKE LOGIC CONTROL] (BLC)
BRH | Brake hidden | 16#2742 = 10050 | 16#2046/33 | 16#93/01/33 = 147/01/51 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
BRR | Current ramp time | 16#271F = 10015 | 16#2046/10 | 16#93/01/10 = 147/01/16 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 5.00 s | [Current ramp time] (BRR) | [BRAKE LOGIC CONTROL] (BLC)
HSO | High speed hoisting | 16#300D = 12301 | 16#205D/2 | 16#9E/01/66 = 158/01/102 | HSO | Configuration and settings | R/WS | WORD (Enumeration) | - | [Inactive] NO |  | [High speed hoisting] (HSO) | [HIGH SPEED HOISTING] (HSH)
COF | Motor speed coefficient | 16#300F = 12303 | 16#205D/4 | 16#9E/01/68 = 158/01/104 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 100 % | [Motor speed coeff.] (COF) | [HIGH SPEED HOISTING] (HSH)
COR | Generator speed coefficient | 16#3010 = 12304 | 16#205D/5 | 16#9E/01/69 = 158/01/105 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 50 % | 0 % ... 100 % | [Gen. speed coeff] (COR) | [HIGH SPEED HOISTING] (HSH)
TOS | Load measuring time | 16#3013 = 12307 | 16#205D/8 | 16#9E/01/6C = 158/01/108 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.50 s | 0.10 s ... 65.00 s | [Load measuring tm.] (TOS) | [HIGH SPEED HOISTING] (HSH)
OSP | Measurement speed | 16#3011 = 12305 | 16#205D/6 | 16#9E/01/6A = 158/01/106 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 40.0 Hz | 0.0 Hz ... 599.0 Hz | [Measurement spd] (OSP) | [HIGH SPEED HOISTING] (HSH)
CLO | High speed I Limit | 16#300E = 12302 | 16#205D/3 | 16#9E/01/67 = 158/01/103 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | Refer to programming manual | 0.0 A ... 6553.5 A | [High speed I Limit] (CLO) | [HIGH SPEED HOISTING] (HSH)
SCL | Current limit. frequency | 16#3012 = 12306 | 16#205D/7 | 16#9E/01/6B = 158/01/107 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 40.0 Hz | 0.0 Hz ... 599.0 Hz | [I Limit. frequency] (SCL) | [HIGH SPEED HOISTING] (HSH)
RSTL | Rope slack torque level | 16#3022 = 12322 | 16#205D/17 | 16#9E/01/7B = 158/01/123 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [Rope slack trq level] (RSTL) | [HIGH SPEED HOISTING] (HSH)
RSD | Rope slack configuration | 16#3021 = 12321 | 16#205D/16 | 16#9E/01/7A = 158/01/122 | RSD | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Rope slack config.] (RSD) | [HIGH SPEED HOISTING] (HSH)
PIF | PI fdbk assignment | 16#2E7D = 11901 | 16#2059/2 | 16#9C/01/66 = 156/01/102 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [PID feedback ass.] (PIF) | [PID REGULATOR] (PID)
PIF1 | Minimum PID feedback | 16#2E80 = 11904 | 16#2059/5 | 16#9C/01/69 = 156/01/105 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 100 | 0 ... 32767 | [Min PID feedback] (PIF1) | [PID REGULATOR] (PID)
PIF2 | Maximum PID feedback | 16#2E81 = 11905 | 16#2059/6 | 16#9C/01/6A = 156/01/106 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 1000 | 0 ... 32767 | [Max PID feedback] (PIF2) | [PID REGULATOR] (PID)
PIP1 | Minimum PID reference | 16#2E82 = 11906 | 16#2059/7 | 16#9C/01/6B = 156/01/107 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 150 | 0 ... 32767 | [Min PID reference] (PIP1) | [PID REGULATOR] (PID)
PIP2 | Maximum PID reference | 16#2E83 = 11907 | 16#2059/8 | 16#9C/01/6C = 156/01/108 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 900 | 0 ... 32767 | [Max PID reference] (PIP2) | [PID REGULATOR] (PID)
PII | Internal reference PI | 16#2E84 = 11908 | 16#2059/9 | 16#9C/01/6D = 156/01/109 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Act. internal PID ref.] (PII) | [PID REGULATOR] (PID)
RPI | Internal PI reference | 16#2E90 = 11920 | 16#2059/15 | 16#9C/01/79 = 156/01/121 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 150 | 0 ... 32767 | [Internal PID ref.] (RPI) | [SPEED REFERENCE] (rEF) [MONIT. PI ] (MPI) [PID REGULATOR] (PID)
RPG | PI Proportional gain | 16#2EA5 = 11941 | 16#2059/2A | 16#9C/01/8E = 156/01/142 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 | 1.00 | 0.01 ... 100.00 | [PID prop. gain] (RPG) | [SETTINGS] (SET) [PID REGULATOR] (PID)
RIG | Integral gain PI regulator | 16#2EA6 = 11942 | 16#2059/2B | 16#9C/01/8F = 156/01/143 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 | 1.00 | 0.01 ... 100.00 | [PID integral gain] (RIG) | [SETTINGS] (SET) [PID REGULATOR] (PID)
RDG | PID derivative gain | 16#2EA7 = 11943 | 16#2059/2C | 16#9C/01/90 = 156/01/144 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 | 0.00 | 0.00 ... 100.00 | [PID derivative gain] (RDG) | [SETTINGS] (SET) [PID REGULATOR] (PID)
PRP | PID ramp | 16#2ED0 = 11984 | 16#2059/55 | 16#9C/01/B9 = 156/01/185 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 99.9 s | [PID ramp] (PRP) | [SETTINGS] (SET) [PID REGULATOR] (PID)
PIC | PID correction reverse | 16#2EA4 = 11940 | 16#2059/29 | 16#9C/01/8D = 156/01/141 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [PID correct. reverse] (PIC) | [PID REGULATOR] (PID)
POL | PID regulator min. output | 16#2EB0 = 11952 | 16#2059/35 | 16#9C/01/99 = 156/01/153 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | -599.0 Hz ... 599.0 Hz | [Min PID output] (POL) | [SETTINGS] (SET) [PID REGULATOR] (PID)
POH | Max PID output | 16#2EB1 = 11953 | 16#2059/36 | 16#9C/01/9A = 156/01/154 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 60.0 Hz | 0.0 Hz ... 599.0 Hz | [Max PID output] (POH) | [SETTINGS] (SET) [PID REGULATOR] (PID)
PAL | Minimum fdbk alarm | 16#2EB9 = 11961 | 16#2059/3E | 16#9C/01/A2 = 156/01/162 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 100 | 0 ... 65535 | [Min fbk alarm] (PAL) | [SETTINGS] (SET) [PID REGULATOR] (PID)
PAH | Maximum fdbk alarm | 16#2EBA = 11962 | 16#2059/3F | 16#9C/01/A3 = 156/01/163 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 1000 | 0 ... 65535 | [Max fbk alarm] (PAH) | [SETTINGS] (SET) [PID REGULATOR] (PID)
PER | PID error alarm | 16#2EBB = 11963 | 16#2059/40 | 16#9C/01/A4 = 156/01/164 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 100 | 0 ... 65535 | [PID error Alarm] (PER) | [SETTINGS] (SET) [PID REGULATOR] (PID)
PIS | PID integral reset | 16#2EA8 = 11944 | 16#2059/2D | 16#9C/01/91 = 156/01/145 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [PID integral reset] (PIS) | [PID REGULATOR] (PID)
FPI | Speed ref. assignment | 16#2EAE = 11950 | 16#2059/33 | 16#9C/01/97 = 156/01/151 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Speed ref. assign.] (FPI) | [PID REGULATOR] (PID)
PSR | PID speed input % ref | 16#2EAF = 11951 | 16#2059/34 | 16#9C/01/98 = 156/01/152 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 1 % ... 100 % | [Speed input %] (PSR) | [SETTINGS] (SET) [PID REGULATOR] (PID)
PAU | Auto/Manual select input | 16#2EC2 = 11970 | 16#2059/47 | 16#9C/01/AB = 156/01/171 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Auto/Manual assign.] (PAU) | [PID REGULATOR] (PID)
PIM | Manual reference | 16#2EB2 = 11954 | 16#2059/37 | 16#9C/01/9B = 156/01/155 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Manual reference] (PIM) | [PID REGULATOR] (PID)
TLS | Low speed time out | 16#2DB5 = 11701 | 16#2057/2 | 16#9B/01/66 = 155/01/102 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 999.9 s | [Low speed time out] (TLS) | [SETTINGS] (SET) [PID REGULATOR] (PID)
PR2 | 2 preset PID ref assign. | 16#2E85 = 11909 | 16#2059/A | 16#9C/01/6E = 156/01/110 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [2 preset PID ref.] (PR2) | [PID PRESET REFERENCES] (PRI)
PR4 | 4 preset PID ref assign. | 16#2E86 = 11910 | 16#2059/B | 16#9C/01/6F = 156/01/111 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [4 preset PID ref.] (PR4) | [PID PRESET REFERENCES] (PRI)
RP2 | 2nd PI preset reference | 16#2E91 = 11921 | 16#2059/16 | 16#9C/01/7A = 156/01/122 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 300 | 0 ... 32767 | [Preset ref. PID 2] (RP2) | [SETTINGS] (SET) [PID PRESET REFERENCES] (PRI)
RP3 | 3rd PI preset reference | 16#2E92 = 11922 | 16#2059/17 | 16#9C/01/7B = 156/01/123 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 600 | 0 ... 32767 | [Preset ref. PID 3] (RP3) | [SETTINGS] (SET) [PID PRESET REFERENCES] (PRI)
RP4 | 4th PI preset reference | 16#2E93 = 11923 | 16#2059/18 | 16#9C/01/7C = 156/01/124 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 900 | 0 ... 32767 | [Preset ref. PID 4] (RP4) | [SETTINGS] (SET) [PID PRESET REFERENCES] (PRI)
TLA | Torque limit. activation | 16#23FA = 9210 | 16#203E/B | 16#8F/01/0B = 143/01/11 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Torque limit. activ.] (TLA) | [TORQUE LIMITATION] (TOL)
INTP | Torque increment | 16#23FF = 9215 | 16#203E/10 | 16#8F/01/10 = 143/01/16 | INCPER | Configuration and settings | R/WS | WORD (Enumeration) | - | [1%] 1 |  | [Torque increment] (INTP) | [TORQUE LIMITATION] (TOL)
TLIM | Motoring torque limit | 16#23FB = 9211 | 16#203E/C | 16#8F/01/0C = 143/01/12 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 100 | 0 ... 3000 | [Motoring torque lim] (TLIM) | [SETTINGS] (SET) [TORQUE LIMITATION] (TOL)
TLIG | Generator torque limit | 16#23FC = 9212 | 16#203E/D | 16#8F/01/0D = 143/01/13 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 100 | 0 ... 3000 | [Gen. torque lim] (TLIG) | [SETTINGS] (SET) [TORQUE LIMITATION] (TOL)
TAA | Torque reference assign. | 16#23FE = 9214 | 16#203E/F | 16#8F/01/0F = 143/01/15 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Torque ref. assign.] (TAA) | [TORQUE LIMITATION] (TOL)
TLC | Torque analog limit. activ | 16#23FD = 9213 | 16#203E/E | 16#8F/01/0E = 143/01/14 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Yes] YES |  | [Analog limit. act.] (TLC) | [TORQUE LIMITATION] (TOL)
LC2 | I limit 2 input assign. | 16#23F2 = 9202 | 16#203E/3 | 16#8F/01/03 = 143/01/03 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Current limit 2] (LC2) | [2nd CURRENT LIMIT.] (CLI)
CL2 | Internal current limit 2 | 16#23F3 = 9203 | 16#203E/4 | 16#8F/01/04 = 143/01/04 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | Refer to programming manual | 0.0 A ... 6553.5 A | [I Limit. 2 value] (CL2) | [SETTINGS] (SET) [2nd CURRENT LIMIT.] (CLI)
LLC | Line contactor control | 16#3522 = 13602 | 16#206A/3 | 16#A5/01/03 = 165/01/03 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [Line contactor ass.] (LLC) | [LINE Contactor Command] (LLC)
LES | E stop assignment | 16#3521 = 13601 | 16#206A/2 | 16#A5/01/02 = 165/01/02 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Drive lock ] (LES) | [LINE Contactor Command] (LLC)
LCT | Time-out after cont. activ. | 16#3523 = 13603 | 16#206A/4 | 16#A5/01/04 = 165/01/04 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 5 s | 5 s ... 999 s | [Mains V. time out ] (LCT) | [LINE Contactor Command] (LLC)
SAF | Fwd stop limit input assig | 16#30D5 = 12501 | 16#205F/2 | 16#9F/01/66 = 159/01/102 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Stop FW limit sw.] (SAF) | [POSITIONING BY SENSORS] (LPO)
SAR | RV stop limit input assign | 16#30D6 = 12502 | 16#205F/3 | 16#9F/01/67 = 159/01/103 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Stop RV limit sw.] (SAR) | [POSITIONING BY SENSORS] (LPO)
DAF | Forward slowdown limit | 16#30D7 = 12503 | 16#205F/4 | 16#9F/01/68 = 159/01/104 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Slowdown forward] (DAF) | [POSITIONING BY SENSORS] (LPO)
DAR | Reverse slowdown limit | 16#30D8 = 12504 | 16#205F/5 | 16#9F/01/69 = 159/01/105 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Slowdown reverse] (DAR) | [POSITIONING BY SENSORS] (LPO)
CLS | Disable limit switch | 16#30DB = 12507 | 16#205F/8 | 16#9F/01/6C = 159/01/108 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Disable limit sw.] (CLS) | [POSITIONING BY SENSORS] (LPO)
PAS | Stop type | 16#30DA = 12506 | 16#205F/7 | 16#9F/01/6B = 159/01/107 | STT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Stop on decel. ramp] RMP |  | [Stop type] (PAS) | [POSITIONING BY SENSORS] (LPO)
DSF | Deceleration type | 16#30D9 = 12505 | 16#205F/6 | 16#9F/01/6A = 159/01/106 | DSF | Configuration and settings | R/WS | WORD (Enumeration) | - | [Standard] STD |  | [Deceleration type] (DSF) | [POSITIONING BY SENSORS] (LPO)
STD | Stop distance | 16#30E9 = 12521 | 16#205F/16 | 16#9F/01/7A = 159/01/122 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 m | 0.00 m | 0.00 m ... 10.00 m | [Stop distance] (STD) | [POSITIONING BY SENSORS] (LPO)
NLS | Rated linear speed | 16#30DF = 12511 | 16#205F/C | 16#9F/01/70 = 159/01/112 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 m/s | 1.00 m/s | 0.20 m/s ... 5.00 m/s | [Rated linear speed] (NLS) | [POSITIONING BY SENSORS] (LPO)
SFD | Distance stop corrector | 16#30EA = 12522 | 16#205F/17 | 16#9F/01/7B = 159/01/123 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 100 % | 50 % ... 200 % | [Stop corrector] (SFD) | [POSITIONING BY SENSORS] (LPO)
CHM | Multimotors selection | 16#1F59 = 8025 | 16#2032/1A | 16#89/01/1A = 137/01/26 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Multimotors] (CHM) | [MULTIMOTORS/CONFIG.] (MMC)
CNF1 | 2 configurations assignt. | 16#1F55 = 8021 | 16#2032/16 | 16#89/01/16 = 137/01/22 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [2 Configurations] (CNF1) | [MULTIMOTORS/CONFIG.] (MMC)
CNF2 | 3 configurations assignt. | 16#1F56 = 8022 | 16#2032/17 | 16#89/01/17 = 137/01/23 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [3 Configurations] (CNF2) | [MULTIMOTORS/CONFIG.] (MMC)
TUL | Auto-tune input assign. | 16#258A = 9610 | 16#2042/B | 16#91/01/0B = 145/01/11 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Auto-tune assign.] (TUL) | [AUTO TUNING BY LI] (TNL)
RSF | Fault reset input assign. | 16#1BD4 = 7124 | 16#2029/19 | 16#84/01/7D = 132/01/125 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Fault reset] (RSF) | [FAULT RESET] (RST)
RP | Product reset | 16#1BD8 = 7128 | 16#2029/1D | 16#84/01/81 = 132/01/129 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Product reset] (RP) | [FAULT RESET] (RST)
RPA | Product reset assignment | 16#1BD9 = 7129 | 16#2029/1E | 16#84/01/82 = 132/01/130 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Product reset assig.] (RPA) | [FAULT RESET] (RST)
ATR | Automatic restart | 16#1BD2 = 7122 | 16#2029/17 | 16#84/01/7B = 132/01/123 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Automatic restart] (ATR) | [AUTOMATIC RESTART] (ATR)
TAR | Max. restart duration | 16#1BD3 = 7123 | 16#2029/18 | 16#84/01/7C = 132/01/124 | DUR | Configuration and settings | R/WS | WORD (Enumeration) | - | [5 minutes] 5 |  | [Max. restart time] (TAR) | [AUTOMATIC RESTART] (ATR)
FLR | Catch a spinning load | 16#0C26 = 3110 | 16#2001/B | 16#70/01/6F = 112/01/111 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Catch on the fly] (FLR) | [CATCH ON THE FLY] (FLR)
THT | Thermal protection type | 16#258C = 9612 | 16#2042/D | 16#91/01/0D = 145/01/13 | THT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Self cooled motor] ACL |  | [Motor protect. type] (THT) | [MOTOR THERMAL PROT.] (THT)
TTD | Motor thermal threshold | 16#2AFA = 11002 | 16#2050/3 | 16#98/01/03 = 152/01/03 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 118 % | [Motor therm. level] (TTD) | [SETTINGS] (SET) [MOTOR THERMAL PROT.] (THT) [THERMAL ALARM STOP] (SAT)
TTD2 | Motor 2 thermal threshold | 16#2AFE = 11006 | 16#2050/7 | 16#98/01/07 = 152/01/07 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 118 % | [Motor2 therm. level] (TTD2) | [MOTOR THERMAL PROT.] (THT) [THERMAL ALARM STOP] (SAT)
TTD3 | Motor 3 thermal threshold | 16#2AFF = 11007 | 16#2050/8 | 16#98/01/08 = 152/01/08 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 118 % | [Motor3 therm. level] (TTD3) | [MOTOR THERMAL PROT.] (THT) [THERMAL ALARM STOP] (SAT)
OLL | Stop type - motor o/load | 16#1B61 = 7009 | 16#2028/A | 16#84/01/0A = 132/01/10 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop on fault] YES |  | [Overload fault mgt] (OLL) | [MOTOR THERMAL PROT.] (THT)
OPL | Output phase loss | 16#258B = 9611 | 16#2042/C | 16#91/01/0C = 145/01/12 | OPL | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Output Phase Loss] (OPL) | [OUTPUT PHASE LOSS] (OPL)
ODT | Output ph detection time | 16#1BA9 = 7081 | 16#2028/52 | 16#84/01/52 = 132/01/82 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.5 s ... 10.0 s | [OutPh time detect] (ODT) | [OUTPUT PHASE LOSS] (OPL)
IPL | Stop type - I/P phase loss | 16#1B5A = 7002 | 16#2028/3 | 16#84/01/03 = 132/01/03 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Input phase loss] (IPL) | [INPUT PHASE LOSS] (IPL) [SIMPLY START] (SIM) [DC Bus] (DCC)
OHL | Stop type - drive o/temp | 16#1B60 = 7008 | 16#2028/9 | 16#84/01/09 = 132/01/09 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop on fault] YES |  | [Overtemp fault mgt] (OHL) | [DRIVE OVERHEAT] (OHL)
THA | Drive therm. state alarm | 16#2B01 = 11009 | 16#2050/A | 16#98/01/0A = 152/01/10 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 118 % | [Drv therm. state al] (THA) | [DRIVE OVERHEAT] (OHL) [THERMAL ALARM STOP] (SAT)
ETF | External fault input | 16#1BDB = 7131 | 16#2029/20 | 16#84/01/84 = 132/01/132 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [External fault ass.] (ETF) | [EXTERNAL FAULT] (ETF)
EPL | Stop type - external fault | 16#1B5E = 7006 | 16#2028/7 | 16#84/01/07 = 132/01/07 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop on fault] YES |  | [External fault mgt] (EPL) | [EXTERNAL FAULT] (ETF)
USB | Undervolt fault manage | 16#35EB = 13803 | 16#206C/4 | 16#A6/01/04 = 166/01/04 | USB | Configuration and settings | R/WS | WORD (Enumeration) | - | [Standard fault] 0 |  | [UnderV. fault mgt] (USB) | [UNDERVOLTAGE MGT] (USB)
URES | Evacuation mains voltage | 16#35E9 = 13801 | 16#206C/2 | 16#A6/01/02 = 166/01/02 | URES | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Mains voltage] (URES) | [UNDERVOLTAGE MGT] (USB) [DC Bus] (DCC)
USL | Undervoltage level | 16#35EA = 13802 | 16#206C/3 | 16#A6/01/03 = 166/01/03 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | Refer to programming manual | 100 V ... 304 V | [Undervoltage level] (USL) | [UNDERVOLTAGE MGT] (USB) [DC Bus] (DCC)
UST | Undervoltage time out | 16#35EC = 13804 | 16#206C/5 | 16#A6/01/05 = 166/01/05 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 0.2 s | 0.2 s ... 999.9 s | [Undervolt. time out] (UST) | [UNDERVOLTAGE MGT] (USB)
STP | Ctrld stop on power loss | 16#1B5C = 7004 | 16#2028/5 | 16#84/01/05 = 132/01/05 | STP | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop with fault] NO |  | [UnderV. prevention] (STP) | [UNDERVOLTAGE MGT] (USB)
TSM | Undervolt. restart time | 16#35F5 = 13813 | 16#206C/E | 16#A6/01/0E = 166/01/14 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 1.0 s | 1.0 s ... 999.9 s | [UnderV. restart tm] (TSM) | [UNDERVOLTAGE MGT] (USB)
UPL | Under V prevention level | 16#35F3 = 13811 | 16#206C/C | 16#A6/01/0C = 166/01/12 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | Refer to programming manual | 141 V ... 368 V | [Prevention level] (UPL) | [UNDERVOLTAGE MGT] (USB)
SDD | Load slip detection | 16#1B5D = 7005 | 16#2028/6 | 16#84/01/06 = 132/01/06 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [Yes] YES |  | [Load slip detection] (SDD) | [ENCODER FAULT] (SDD)
STM | Maximum stop time | 16#35F6 = 13814 | 16#206C/F | 16#A6/01/0F = 166/01/15 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 1.00 s | 0.01 s ... 60.00 s | [Max stop time] (STM) | [UNDERVOLTAGE MGT] (USB)
TBS | DC bus maintain time | 16#35F4 = 13812 | 16#206C/D | 16#A6/01/0D = 166/01/13 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 9999 s | 1 s ... 9999 s | [DC bus maintain tm] (TBS) | [UNDERVOLTAGE MGT] (USB)
STRT | IGBT test | 16#0C28 = 3112 | 16#2001/D | 16#70/01/71 = 112/01/113 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [IGBT test] (STRT) | [IGBT TESTS] (TIT)
LFL3 | Stop type - loss AI3 | 16#1B65 = 7013 | 16#2028/E | 16#84/01/0E = 132/01/14 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ignore phase loss] NO |  | [AI3 4-20mA loss] (LFL3) | [4-20mA LOSS] (LFL)
INH | Fault inhibit input | 16#1BD5 = 7125 | 16#2029/1A | 16#84/01/7E = 132/01/126 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Fault inhibit assign.] (INH) | [FAULT INHIBITION] (INH)
CLL | Stop type - network fault | 16#1B67 = 7015 | 16#2028/10 | 16#84/01/10 = 132/01/16 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop on fault] YES |  | [Network fault mgt] (CLL) | [COM. FAULT MANAGEMENT] (CLL)
COL | Stop type - CANopen fault | 16#1B63 = 7011 | 16#2028/C | 16#84/01/0C = 132/01/12 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop on fault] YES |  | [CANopen fault mgt] (COL) | [COM. FAULT MANAGEMENT] (CLL)
SLL | Stop type - Modbus SLF | 16#1B62 = 7010 | 16#2028/B | 16#84/01/0B = 132/01/11 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop on fault] YES |  | [Modbus fault mgt] (SLL) | [COM. FAULT MANAGEMENT] (CLL)
SSB | Stop type - Torque/I limit | 16#2418 = 9240 | 16#203E/29 | 16#8F/01/29 = 143/01/41 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ignore phase loss] NO |  | [Trq/I limit. stop] (SSB) | [Torque OR I LIM. DETECT] (TID)
STO | Torque/I limit. time out | 16#2419 = 9241 | 16#203E/2A | 16#8F/01/2A = 143/01/42 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 1000 ms | 0 ms ... 9999 ms | [Trq/I limit. time out] (STO) | [Torque OR I LIM. DETECT] (TID)
TNL | Auto-tuning fault config. | 16#1B64 = 7012 | 16#2028/D | 16#84/01/0D = 132/01/13 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop on fault] YES |  | [Autotune fault mgt] (TNL) | [AUTO TUNING FAULT] (TNF)
PPI | Pairing password | 16#36B1 = 14001 | 16#206E/2 | 16#A7/01/02 = 167/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 9999 | [Pairing password] (PPI) | [CARDS PAIRING ] (PPI)
LFF | Fall back speed | 16#1BA8 = 7080 | 16#2028/51 | 16#84/01/51 = 132/01/81 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Fallback speed] (LFF) | [FALLBACK SPEED] (LFF)
FQF | Frequency meter | 16#3909 = 14601 | 16#2074/2 | 16#AA/01/02 = 170/01/02 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Frequency meter] (FQF) | [FREQUENCY METER] (FQF)
FQC | Pulse scaling divisor | 16#390A = 14602 | 16#2074/3 | 16#AA/01/03 = 170/01/03 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 | 1.0 | 1.0 ... 100.0 | [Pulse scal. divisor] (FQC) | [FREQUENCY METER] (FQF)
FQA | Overspd. pulse threshold | 16#390C = 14604 | 16#2074/5 | 16#AA/01/05 = 170/01/05 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 Hz | 0 Hz | 0 Hz ... 20000 Hz | [Overspd. pulse thd.] (FQA) | [FREQUENCY METER] (FQF)
TDS | Pulse Overspeed delay | 16#390D = 14605 | 16#2074/6 | 16#AA/01/06 = 170/01/06 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 10.0 s | [Pulse overspd delay] (TDS) | [FREQUENCY METER] (FQF)
FDT | Level freq. pulse ctrl | 16#390E = 14606 | 16#2074/7 | 16#AA/01/07 = 170/01/07 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Level fr. pulse ctrl] (FDT) | [FREQUENCY METER] (FQF)
FQT | Pulse threshold wo Run | 16#390F = 14607 | 16#2074/8 | 16#AA/01/08 = 170/01/08 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 Hz | 0 Hz | 0 Hz ... 1000 Hz | [Pulse thd. wo Run] (FQT) | [FREQUENCY METER] (FQF)
TLD | Dynamic load time | 16#3018 = 12312 | 16#205D/D | 16#9E/01/71 = 158/01/113 |  | Configuration and settings | R/WS | INT (Signed16) | 0.01 s | -0.01 s | -0.01 s ... 10.00 s | [Dynamic load time] (TLD) | [DYNAMIC LOAD DETECT.] (DLD)
DLD | Dynamic load threshold | 16#3017 = 12311 | 16#205D/C | 16#9E/01/70 = 158/01/112 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 100 % | 1 % ... 100 % | [Dyn. load threshold] (DLD) | [DYNAMIC LOAD DETECT.] (DLD)
DLB | Dynamic load Mgt. | 16#3019 = 12313 | 16#205D/E | 16#9E/01/72 = 158/01/114 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop on fault] YES |  | [Dyn. load Mgt.] (DLB) | [DYNAMIC LOAD DETECT.] (DLD)
NCA1 | Scan output 1 address | 16#31B1 = 12721 | 16#2061/16 | 16#A0/01/7A = 160/01/122 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 8501 | 0 ... 65535
NCA2 | Scan output 2 address | 16#31B2 = 12722 | 16#2061/17 | 16#A0/01/7B = 160/01/123 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 8602 | 0 ... 65535
NCA3 | Scan output 3 address | 16#31B3 = 12723 | 16#2061/18 | 16#A0/01/7C = 160/01/124 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NCA4 | Scan output 4 address | 16#31B4 = 12724 | 16#2061/19 | 16#A0/01/7D = 160/01/125 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NCA5 | Scan output 5 address | 16#31B5 = 12725 | 16#2061/1A | 16#A0/01/7E = 160/01/126 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NCA6 | Scan output 6 address | 16#31B6 = 12726 | 16#2061/1B | 16#A0/01/7F = 160/01/127 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NCA7 | Scan output 7 address | 16#31B7 = 12727 | 16#2061/1C | 16#A0/01/80 = 160/01/128 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NCA8 | Scan output 8 address | 16#31B8 = 12728 | 16#2061/1D | 16#A0/01/81 = 160/01/129 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA1 | Scan input 1 address | 16#319D = 12701 | 16#2061/2 | 16#A0/01/66 = 160/01/102 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 3201 | 0 ... 65535
NMA2 | Scan input 2 address | 16#319E = 12702 | 16#2061/3 | 16#A0/01/67 = 160/01/103 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 8604 | 0 ... 65535
NMA3 | Scan input 3 address | 16#319F = 12703 | 16#2061/4 | 16#A0/01/68 = 160/01/104 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA4 | Scan input 4 address | 16#31A0 = 12704 | 16#2061/5 | 16#A0/01/69 = 160/01/105 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA5 | Scan input 5 address | 16#31A1 = 12705 | 16#2061/6 | 16#A0/01/6A = 160/01/106 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA6 | Scan input 6 address | 16#31A2 = 12706 | 16#2061/7 | 16#A0/01/6B = 160/01/107 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA7 | Scan input 7 address | 16#31A3 = 12707 | 16#2061/8 | 16#A0/01/6C = 160/01/108 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA8 | Scan input 8 address | 16#31A4 = 12708 | 16#2061/9 | 16#A0/01/6D = 160/01/109 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMA1 | Scan input 1 address | 16#3C29 = 15401 | 16#207C/2 | 16#AE/01/02 = 174/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 3201 | 0 ... 65535
OMA2 | Scan input 2 address | 16#3C2A = 15402 | 16#207C/3 | 16#AE/01/03 = 174/01/03 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 8604 | 0 ... 65535
OMA3 | Scan input 3 address | 16#3C2B = 15403 | 16#207C/4 | 16#AE/01/04 = 174/01/04 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMA4 | Scan input 4 address | 16#3C2C = 15404 | 16#207C/5 | 16#AE/01/05 = 174/01/05 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMA5 | Scan input 5 address | 16#3C2D = 15405 | 16#207C/6 | 16#AE/01/06 = 174/01/06 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMA6 | Scan input 6 address | 16#3C2E = 15406 | 16#207C/7 | 16#AE/01/07 = 174/01/07 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCA1 | Scan output 1 address | 16#3C3D = 15421 | 16#207C/16 | 16#AE/01/16 = 174/01/22 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 8501 | 0 ... 65535
OCA2 | Scan output 2 address | 16#3C3E = 15422 | 16#207C/17 | 16#AE/01/17 = 174/01/23 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 8602 | 0 ... 65535
OCA3 | Scan output 3 address | 16#3C3F = 15423 | 16#207C/18 | 16#AE/01/18 = 174/01/24 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCA4 | Scan output 4 address | 16#3C40 = 15424 | 16#207C/19 | 16#AE/01/19 = 174/01/25 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCA5 | Scan output 5 address | 16#3C41 = 15425 | 16#207C/1A | 16#AE/01/1A = 174/01/26 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCA6 | Scan output 6 address | 16#3C42 = 15426 | 16#207C/1B | 16#AE/01/1B = 174/01/27 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
ADD | Drive modbus address | 16#1771 = 6001 | 16#201E/2 | 16#7F/01/02 = 127/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 247 | [Modbus Address] (ADD) | [MODBUS NETWORK] (MD1)
AMOC | Mdb add comm. card | 16#19FB = 6651 | 16#2024/34 | 16#82/01/34 = 130/01/52 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 247 | [Modbus add Com.C.] (AMOC) | [MODBUS NETWORK] (MD1)
TBR | Modbus baud rate | 16#1773 = 6003 | 16#201E/4 | 16#7F/01/04 = 127/01/04 | TBR | Configuration and settings | R/WS | WORD (Enumeration) | - | [19.2 Kbps] 19200 |  | [Modbus baud rate] (TBR) | [MODBUS NETWORK] (MD1)
TFO | Modbus com format | 16#1774 = 6004 | 16#201E/5 | 16#7F/01/05 = 127/01/05 | FOR | Configuration and settings | R/WS | WORD (Enumeration) | - | [8bit even parity 1stop bit] 8E1 |  | [Modbus format] (TFO) | [MODBUS NETWORK] (MD1)
TTO | Modbus time out | 16#1775 = 6005 | 16#201E/6 | 16#7F/01/06 = 127/01/06 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 10.0 s | 0.1 s ... 30.0 s | [Modbus time out] (TTO) | [MODBUS NETWORK] (MD1)
ADCO | Drive CANopen address | 16#17A3 = 6051 | 16#201E/34 | 16#7F/01/34 = 127/01/52 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 127 | [CANopen address] (ADCO) | [CANopen ] (CNO)
BDCO | CANopen baudrate | 16#17A5 = 6053 | 16#201E/36 | 16#7F/01/36 = 127/01/54 | BDCO | Configuration and settings | R/WS | WORD (Enumeration) | - | [Baud rate 250kbps] 250K |  | [CANopen bit rate] (BDCO) | [CANopen ] (CNO)
ERCO | Error code CANopen | 16#17A8 = 6056 | 16#201E/39 | 16#7F/01/39 = 127/01/57 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 5 | [Error code] (ERCO) | [CANopen MAP] (CNM) [CANopen ] (CNO)
FLO | Forced local mode assign | 16#20EF = 8431 | 16#2036/20 | 16#8B/01/20 = 139/01/32 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Forced local assign.] (FLO) | [FORCED LOCAL] (LCF)
FLOC | Forced local ref. assign. | 16#20F0 = 8432 | 16#2036/21 | 16#8B/01/21 = 139/01/33 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Forced local Ref.] (FLOC) | [FORCED LOCAL] (LCF)
FLOT | Time-out forc. local | 16#20F1 = 8433 | 16#2036/22 | 16#8B/01/22 = 139/01/34 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 10.0 s | 0.1 s ... 30.0 s | [Time-out forc. local] (FLOT) | [FORCED LOCAL] (LCF)
ADRC | Drive address | 16#19C9 = 6601 | 16#2024/2 | 16#82/01/02 = 130/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | Refer to programming manual | 0 ... 65535 | [Address] (ADRC) | [COMMUNICATION CARD] (CBD)
PRFL | PPO profile used | 16#1A09 = 6665 | 16#2024/42 | 16#82/01/42 = 130/01/66 | PRFL | Configuration and settings | R/W | WORD (Enumeration) | - | Refer to programming manual |  | [PPO profile used] (PRFL) | [COMMUNICATION CARD] (CBD)
DPMA | DP Master Active | 16#1A0A = 6666 | 16#2024/43 | 16#82/01/43 = 130/01/67 | DPMA | Communication parameters | R/W | WORD (Enumeration) | - | [MCL1] 1 |  | [DP Master Active] (DPMA) | [COMMUNICATION CARD] (CBD)
ECSA | EtherCAT second address | 16#1A23 = 6691 | 16#2024/5C | 16#82/01/5C = 130/01/92 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [EthCat 2nd addr] (ECSA) | [COMMUNICATION CARD] (CBD)
CIOA | Configured Assembly | 16#1A0B = 6667 | 16#2024/44 | 16#82/01/44 = 130/01/68 | CIOA | Configuration and settings | R/W | WORD (Enumeration) | - | [21/71] 21 |  | [Conf. Assembly] (CIOA) | [COMMUNICATION CARD] (CBD)
BDR | Comm. option baud rate | 16#19CB = 6603 | 16#2024/4 | 16#82/01/04 = 130/01/04 | TBR | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Bit rate] (BDR) | [COMMUNICATION CARD] (CBD)
BDRU | Data rate used | 16#1A04 = 6660 | 16#2024/3D | 16#82/01/3D = 130/01/61 | TBR | Configuration and settings | R/W | WORD (Enumeration) | - | [Automatic] AUTO |  | [Data rate used] (BDRU) | [COMMUNICATION CARD] (CBD)
RDS | Rate and duplex setting | 16#FAFB = 64251 |  |  | RDS | Configuration and settings | R/W | WORD (Enumeration) | - | [Auto detected] AUTO |  | [Rate setting] (RDS) | [COMMUNICATION CARD] (CBD)
EWE | Enable web and/or email | 16#FB08 = 64264 |  |  |  | Configuration and settings | R/W | WORD (BitString16) | - | 1
ARD | Actual rate and duplex | 16#FB0A = 64266 |  |  | RDS | Configuration and settings | R | WORD (Enumeration) | -
L1D | LI1 on delay | 16#0FA1 = 4001 | 16#200A/2 | 16#75/01/02 = 117/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 200 ms | [LI1 On Delay] (L1D) | [LI1 assignment] (L1A) [LI1 CONFIGURATION] (L1)
R1 | Relay ouput 1 assignment | 16#1389 = 5001 | 16#2014/2 | 16#7A/01/02 = 122/01/02 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [No drive flt] FLT |  | [R1 Assignment] (R1) | [R1 CONFIGURATION] (R1)
R2 | Relay ouput 2 assignment | 16#138A = 5002 | 16#2014/3 | 16#7A/01/03 = 122/01/03 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [R2 Assignment] (R2) | [R2 CONFIGURATION] (R2)
L2D | LI2 on delay | 16#0FA2 = 4002 | 16#200A/3 | 16#75/01/03 = 117/01/03 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 200 ms | [LI2 On Delay] (L2D) | [LI2 assignment] (L2A) [LI2 CONFIGURATION] (L2)
R1D | R1 Delay time | 16#1091 = 4241 | 16#200C/2A | 16#76/01/2A = 118/01/42 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R1 Delay time] (R1D) | [R1 CONFIGURATION] (R1)
R2D | R2 Delay time | 16#1092 = 4242 | 16#200C/2B | 16#76/01/2B = 118/01/43 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R2 Delay time] (R2D) | [R2 CONFIGURATION] (R2)
L3D | LI3 on delay | 16#0FA3 = 4003 | 16#200A/4 | 16#75/01/04 = 117/01/04 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 200 ms | [LI3 On Delay] (L3D) | [LI3 assignment] (L3A) [LI3 CONFIGURATION] (L3)
R1S | R1 Active level | 16#1069 = 4201 | 16#200C/2 | 16#76/01/02 = 118/01/02 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [R1 Active at] (R1S) | [R1 CONFIGURATION] (R1)
R2S | R2 Active level | 16#106A = 4202 | 16#200C/3 | 16#76/01/03 = 118/01/03 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [R2 Active at] (R2S) | [R2 CONFIGURATION] (R2)
L4D | LI4 on delay | 16#0FA4 = 4004 | 16#200A/5 | 16#75/01/05 = 117/01/05 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 200 ms | [LI4 On Delay] (L4D) | [LI4 assignment] (L4A) [LI4 CONFIGURATION] (L4)
R1H | R1 Holding time | 16#107D = 4221 | 16#200C/16 | 16#76/01/16 = 118/01/22 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R1 Holding time] (R1H) | [R1 CONFIGURATION] (R1)
R2H | R2 Holding time | 16#107E = 4222 | 16#200C/17 | 16#76/01/17 = 118/01/23 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R2 Holding time] (R2H) | [R2 CONFIGURATION] (R2)
L5D | LI5 on delay | 16#0FA5 = 4005 | 16#200A/6 | 16#75/01/06 = 117/01/06 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 200 ms | [LI5 On Delay] (L5D) | [LI5 assignment] (L5A) [LI5 CONFIGURATION] (L5)
L6D | LI6 on delay | 16#0FA6 = 4006 | 16#200A/7 | 16#75/01/07 = 117/01/07 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 200 ms | [LI6 On Delay] (L6D) | [LI6 assignment] (L6A) [LI6 CONFIGURATION] (L6)
DO1 | DO1 assignment | 16#13A7 = 5031 | 16#2014/20 | 16#7A/01/20 = 122/01/32 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [DO1 assignment] (DO1) | [DO1 CONFIGURATION] (DO1)
DO1D | DO1 delay time | 16#10B9 = 4281 | 16#200C/52 | 16#76/01/52 = 118/01/82 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [DO1 delay time] (DO1D) | [DO1 CONFIGURATION] (DO1)
DO1H | DO1 holding time | 16#10AF = 4271 | 16#200C/48 | 16#76/01/48 = 118/01/72 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [DO1 holding time] (DO1H) | [DO1 CONFIGURATION] (DO1)
DO1S | DO1 active level | 16#10A5 = 4261 | 16#200C/3E | 16#76/01/3E = 118/01/62 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [DO1 active at] (DO1S) | [DO1 CONFIGURATION] (DO1)
FRHT | FRH high resolution | 16#0C96 = 3222 | 16#2002/17 | 16#71/01/17 = 113/01/23 |  | Configuration and settings | R | INT (Signed16) | 1 |  | -32767 ... 32767
SLCR | LCR without filter | 16#0C98 = 3224 | 16#2002/19 | 16#71/01/19 = 113/01/25 |  | Configuration and settings | R | UINT (Unsigned16) | 0.1 A |  | 0.0 A ... 6553.5 A
SRFR | RFR without filter | 16#0C99 = 3225 | 16#2002/1A | 16#71/01/1A = 113/01/26 |  | Configuration and settings | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz
MMF | Measured output freq. | 16#0C93 = 3219 | 16#2002/14 | 16#71/01/14 = 113/01/20 |  | Configuration and settings | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Measured output fr.] (MMF) | [MONITORING] (MON)
SOTR | Motor torque (% of Cn motor in Q12) without filter | 16#0C9A = 3226 | 16#2002/1B | 16#71/01/1B = 113/01/27 |  | Configuration and settings | R | INT (Signed16) | 1 |  | -32767 ... 32767
SULN | ULN without filter | 16#0C9D = 3229 | 16#2002/1E | 16#71/01/1E = 113/01/30 |  | Configuration and settings | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V
SOPR | OPR without filter | 16#0CDA = 3290 | 16#2002/5B | 16#71/01/5B = 113/01/91 |  | Configuration and settings | R | INT (Signed16) | 1 % |  | -32767 % ... 32767 %
SAI1 | AI1 physical value without filter | 16#14AB = 5291 | 16#2016/5C | 16#7B/01/5C = 123/01/92 |  | Measurement parameters | R | INT (Signed16) | 0.001 V |  | -32.767 V ... 32.767 V
SAI2 | AI2 physical value without filter | 16#14AC = 5292 | 16#2016/5D | 16#7B/01/5D = 123/01/93 |  | Measurement parameters | R | INT (Signed16) | 0.001 V |  | -32.767 V ... 32.767 V
SAI3 | AI3 physical value without filter | 16#14AD = 5293 | 16#2016/5E | 16#7B/01/5E = 123/01/94 |  | Measurement parameters | R | INT (Signed16) | 0.001 mA |  | -32.767 mA ... 32.767 mA
SAO1 | AO1 physical value without filter | 16#14AF = 5295 | 16#2016/60 | 16#7B/01/60 = 123/01/96 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
PGI | Number of pulses | 16#15E4 = 5604 | 16#201A/5 | 16#7D/01/05 = 125/01/05 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 1024 | 100 ... 3600 | [Number of pulses] (PGI) | [ENCODER CONFIGURATION] (IEN)
ENS | Encoder type configure | 16#15E8 = 5608 | 16#201A/9 | 16#7D/01/09 = 125/01/09 | ENS | Configuration and settings | R/WS | WORD (Enumeration) | - | [For signals A/A-/B/B-] AABB |  | [Encoder type] (ENS) | [ENCODER CONFIGURATION] (IEN)
ENU | Encoder usage | 16#15E6 = 5606 | 16#201A/7 | 16#7D/01/07 = 125/01/07 | ENU | Configuration and settings | R/WS | WORD (Enumeration) | - | [Inactive] NO |  | [Encoder usage] (ENU) | [ENCODER CONFIGURATION] (IEN)
ULT | Underld T. Delay Detect. | 16#384B = 14411 | 16#2072/C | 16#A9/01/0C = 169/01/12 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 100 s | [Unld T. Del. Detect] (ULT) | [PROCESS UNDERLOAD] (ULD)
SRB | Hysteresis Freq.Attained | 16#3841 = 14401 | 16#2072/2 | 16#A9/01/02 = 169/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.3 Hz | 0.3 Hz ... 599.0 Hz | [Hysteresis Freq.Att.] (SRB) | [SETTINGS] (SET) [PROCESS UNDERLOAD] (ULD) [PROCESS OVERLOAD] (OLD)
UDL | Underload Management | 16#384C = 14412 | 16#2072/D | 16#A9/01/0D = 169/01/13 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop on fault] YES |  | [Underload Mangmt.] (UDL) | [PROCESS UNDERLOAD] (ULD)
RMUD | Unld. Freq.Thr. Detection | 16#384E = 14414 | 16#2072/F | 16#A9/01/0F = 169/01/15 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Unld. Freq.Thr. Det.] (RMUD) | [SETTINGS] (SET) [PROCESS UNDERLOAD] (ULD)
LUL | Unld.Thr. at O speed | 16#384F = 14415 | 16#2072/10 | 16#A9/01/10 = 169/01/16 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [Unld.Thr.0.Speed] (LUL) | [SETTINGS] (SET) [PROCESS UNDERLOAD] (ULD)
LUN | Unld.Thr. at Nom. speed | 16#3850 = 14416 | 16#2072/11 | 16#A9/01/11 = 169/01/17 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 60 % | 20 % ... 100 % | [Unld.Thr.Nom.Speed] (LUN) | [SETTINGS] (SET) [PROCESS UNDERLOAD] (ULD)
TOL | Overload Time Detect. | 16#3855 = 14421 | 16#2072/16 | 16#A9/01/16 = 169/01/22 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 100 s | [Ovld Time Detect.] (TOL) | [PROCESS OVERLOAD] (OLD)
ODL | Ovld.Proces Management | 16#3856 = 14422 | 16#2072/17 | 16#A9/01/17 = 169/01/23 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop on fault] YES |  | [Ovld.Proces.Mngmt] (ODL) | [PROCESS OVERLOAD] (OLD)
STOS | Safe Torque Off Status | 16#3BDA = 15322 | 16#207B/17 | 16#AD/01/7B = 173/01/123 | STOS | Safety function | R | WORD (Enumeration) | - |  |  | [STO status] (STOS) | [MONIT. SAFETY] (SAF)
AI1I | AI1 input physical image (MAX = 8192) | 16#1466 = 5222 | 16#2016/17 | 16#7B/01/17 = 123/01/23 |  | Measurement parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AI2I | AI2 input physical image (MAX = 8192) | 16#1467 = 5223 | 16#2016/18 | 16#7B/01/18 = 123/01/24 |  | Measurement parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AI3I | AI3 input physical image (MAX = 8192) | 16#1468 = 5224 | 16#2016/19 | 16#7B/01/19 = 123/01/25 |  | Measurement parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AO1I | AO1 output physical image (MAX = 8192) | 16#1483 = 5251 | 16#2016/34 | 16#7B/01/34 = 123/01/52 |  | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
ERR | Ethernet Error Code | 16#FB0E = 64270 |  |  |  | Fault parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Ethernet Error Code] (ERR) | [COMMUNICATION CARD] (CBD)
ETAD | DRIVECOM : Status word | 16#219B = 8603 | 16#2038/4 | 16#8C/01/04 = 140/01/04 |  | Status parameters | R | WORD (BitString16) | -
FTO | Ovld time Before Restart | 16#3857 = 14423 | 16#2072/18 | 16#A9/01/18 = 169/01/24 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 min | 0 min | 0 min ... 6 min | [Overload T.B.Rest.] (FTO) | [SETTINGS] (SET) [PROCESS OVERLOAD] (OLD)
FTU | Unld Time Before Restart | 16#384D = 14413 | 16#2072/E | 16#A9/01/0E = 169/01/14 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 min | 0 min | 0 min ... 6 min | [Underload T.B.Rest.] (FTU) | [SETTINGS] (SET) [PROCESS UNDERLOAD] (ULD)
HSC | High Speed Counter | 16#33FC = 13308 | 16#2067/9 | 16#A3/01/6D = 163/01/109 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
IL1I | Logic inputs physical image (bit0 = LI1 ...) | 16#1451 = 5201 | 16#2016/2 | 16#7B/01/02 = 123/01/02 |  | I/O parameters | R | WORD (BitString16) | -
IPAD | Detected fault code | 16#FB18 = 64280 |  |  |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 5 | [iPar Error Cod] (IPAD) | [COMMUNICATION CARD] (CBD)
LOC | Ovld Threshold Detection | 16#3859 = 14425 | 16#2072/1A | 16#A9/01/1A = 169/01/26 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 110 % | 70 % ... 150 % | [Ovld Detection Thr.] (LOC) | [SETTINGS] (SET) [PROCESS OVERLOAD] (OLD)
PFL | U/F Profile | 16#2598 = 9624 | 16#2042/19 | 16#91/01/19 = 145/01/25 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 20 % | 0 % ... 100 %
SPD | Motor speed | 16#2EE4 = 12004 | 16#205A/5 | 16#9D/01/05 = 157/01/05 |  | Actual values parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Motor speed] (SPD) | [MONIT. MOTOR] (MMO)
TQB | Pulse without Run delay | 16#3910 = 14608 | 16#2074/9 | 16#AA/01/09 = 170/01/09 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 10.0 s | [Pulse wo Run delay] (TQB) | [FREQUENCY METER] (FQF)
PUC | PLC encoder pulse | 16#15EB = 5611 | 16#201A/C | 16#7D/01/0C = 125/01/12 |  | Actual values parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
SPD1 | Output value Customer | 16#2EE8 = 12008 | 16#205A/9 | 16#9D/01/09 = 157/01/09 |  | Actual values parameters | R | UINT (Unsigned16) | 0.01 |  | 0.00 ... 655.35 | [Cust. output value ] (SPD1) | [MONITORING] (MON)
MSTP | With or whithout Memo SToP switch | 16#30EB = 12523 | 16#205F/18 | 16#9F/01/7C = 159/01/124 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [Yes] YES |  | [Memo Stop] (MSTP) | [POSITIONING BY SENSORS] (LPO)
PRST | Priority restart even if switch stop is activated | 16#30EC = 12524 | 16#205F/19 | 16#9F/01/7D = 159/01/125 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Priority restart] (PRST) | [POSITIONING BY SENSORS] (LPO)
INF6 | SHI-C Communication Fault | 16#0E73 = 3699 | 16#2006/64 | 16#73/01/64 = 115/01/100 |  | History parameters | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
HS1 | HMI status | 16#1C99 = 7321 | 16#202B/16 | 16#85/01/7A = 133/01/122 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HS1) | [None] (DP1)
HS2 | HMI status | 16#1C9A = 7322 | 16#202B/17 | 16#85/01/7B = 133/01/123 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HS2) | [None] (DP2)
HS3 | HMI status | 16#1C9B = 7323 | 16#202B/18 | 16#85/01/7C = 133/01/124 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HS3) | [None] (DP3)
HS4 | HMI status | 16#1C9C = 7324 | 16#202B/19 | 16#85/01/7D = 133/01/125 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HS4) | [None] (DP4)
HS5 | HMI status | 16#1C9D = 7325 | 16#202B/1A | 16#85/01/7E = 133/01/126 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HS5) | [None] (DP5)
HS6 | HMI status | 16#1C9E = 7326 | 16#202B/1B | 16#85/01/7F = 133/01/127 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HS6) | [None] (DP6)
HS7 | HMI status | 16#1C9F = 7327 | 16#202B/1C | 16#85/01/80 = 133/01/128 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HS7) | [None] (DP7)
HS8 | HMI status | 16#1CA0 = 7328 | 16#202B/1D | 16#85/01/81 = 133/01/129 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HS8) | [None] (DP8)
MPC | Motor parameter choice | 16#258E = 9614 | 16#2042/F | 16#91/01/0F = 145/01/15 | MPC | Configuration and settings | R/WS | WORD (Enumeration) | - | [Nominal motor Power] NPR |  | [Motor param choice] (MPC) | [ASYNC. MOTOR] (ASY)
RDAE | Ratio D-Axis Current Error | 16#25CC = 9676 | 16#2042/4D | 16#91/01/4D = 145/01/77 |  | Actual values parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [% error EMF sync] (RDAE) | [SYNCHRONOUS MOTOR] (SYN)
TUNU | Auto tuning usage | 16#2593 = 9619 | 16#2042/14 | 16#91/01/14 = 145/01/20 | TUNU | Configuration and settings | R/WS | WORD (Enumeration) | - | [Use the motor thermal evolution] TM |  | [Auto tuning usage] (TUNU) | [ASYNC. MOTOR] (ASY) [SYNCHRONOUS MOTOR] (SYN)
BOO | Boost | 16#3658 = 13912 | 16#206D/D | 16#A6/01/71 = 166/01/113 |  | Configuration and settings | R/WS | INT (Signed16) | 1 % | 0 % | -100 % ... 100 % | [Boost] (BOO) | [MOTOR CONTROL] (DRC)
FAB | Action Boost | 16#3657 = 13911 | 16#206D/C | 16#A6/01/70 = 166/01/112 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Action Boost] (FAB) | [MOTOR CONTROL] (DRC)
FRI | Frequency of the HF injection signal | 16#3CF1 = 15601 | 16#207E/2 | 16#AF/01/02 = 175/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 Hz | 500 Hz | 250 Hz ... 1000 Hz | [HF injection freq.] (FRI) | [SYNCHRONOUS MOTOR] (SYN)
AIV2 | Second virtual AI value | 16#14A3 = 5283 | 16#2016/54 | 16#7B/01/54 = 123/01/84 |  | Setpoint parameters | R/W | INT (Signed16) | 1 | 0 | -8192 ... 8192
AIC2 | AI2 network channel | 16#14A4 = 5284 | 16#2016/55 | 16#7B/01/55 = 123/01/85 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [AI2 net. Channel] (AIC2) | [VIRTUAL AI2] (AV2) [PID REGULATOR] (PID)
AI1L | Analogue input 1 range | 16#1182 = 4482 | 16#200E/53 | 16#77/01/53 = 119/01/83 | AIOL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Positive only] POS |  | [AI1 range] (AI1L) | [AI1 CONFIGURATION] (AI1)
AI2L | Analogue input 2 range | 16#1183 = 4483 | 16#200E/54 | 16#77/01/54 = 119/01/84 | AIOL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Positive only] POS |  | [AI2 range] (AI2L) | [AI2 CONFIGURATION] (AI2)
AI3L | Analogue input 3 range | 16#1184 = 4484 | 16#200E/55 | 16#77/01/55 = 119/01/85 | AIOL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Positive only] POS |  | [AI3 range] (AI3L) | [AI3 CONFIGURATION] (AI3)
APH | Power consumption | 16#0C9E = 3230 | 16#2002/1F | 16#71/01/1F = 113/01/31 |  | Measurement parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Consumption] (APH) | [MONIT. POWER TIME] (PET)
BNS | Program size | 16#3A90 = 14992 | 16#2077/5D | 16#AB/01/C1 = 171/01/193 |  | Function blocks | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Program size] (BNS) | [FB IDENTIFICATION] (FBI) [FB IDENTIFICATION] (FBI)
BNV | Program format version | 16#3A8E = 14990 | 16#2077/5B | 16#AB/01/BF = 171/01/191 |  | Function blocks | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Prg. format version] (BNV) | [FB IDENTIFICATION] (FBI) [FB IDENTIFICATION] (FBI)
BTPI | PIN code | 16#1A11 = 6673 | 16#2024/4A | 16#82/01/4A = 130/01/74 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 9999 | [PIN code] (BTPI) | [BLUETOOTH] (BTH)
BTUA | Bluetooth Activation | 16#1A0E = 6670 | 16#2024/47 | 16#82/01/47 = 130/01/71 | ONOFF | Configuration and settings | R/WS | WORD (Enumeration) | - | [OFF] OFF |  | [Bluetooth Activation] (BTUA) | [BLUETOOTH] (BTH)
BTUC | Bluetooth Visibility | 16#1A0F = 6671 | 16#2024/48 | 16#82/01/48 = 130/01/72 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Bluetooth Visibility] (BTUC) | [BLUETOOTH] (BTH)
BVER | Program version | 16#3A91 = 14993 | 16#2077/5E | 16#AB/01/C2 = 171/01/194 |  | Function blocks | R | UINT (Unsigned16) | 1 |  | 0 ... 255 | [Program version] (BVER) | [FB IDENTIFICATION] (FBI) [FB IDENTIFICATION] (FBI)
CCFG | Customized macro | 16#0BED = 3053 | 16#2000/36 | 16#70/01/36 = 112/01/54 | N_Y | Configuration and settings | R | WORD (Enumeration) | - |  |  | [Customized macro] (CCFG) | [SIMPLY START] (SIM)
CFG | Macro config selection | 16#0BEC = 3052 | 16#2000/35 | 16#70/01/35 = 112/01/53 | CFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Standard Start/Stop] STS |  | [Macro configuration] (CFG) | [CONFIGURATION] (CONF) [SIMPLY START] (SIM)
CIO2 | Configured Assembly | 16#1A0C = 6668 | 16#2024/45 | 16#82/01/45 = 130/01/69 | CIOA | Configuration and settings | R/W | WORD (Enumeration) | - | [21/71] 21 |  | [Conf. Assembly] (CIO2) | [COMMUNICATION CARD] (CBD)
CP1 | Ext weight Point 1Y | 16#2758 = 10072 | 16#2046/49 | 16#93/01/49 = 147/01/73 |  | Configuration and settings | R/WS | INT (Signed16) | 0.1 A | Refer to programming manual | -3276.7 A ... 3276.7 A | [Point 1Y] (CP1) | [EXTERNAL WEIGHT MEAS.] (ELM)
CP2 | Ext weight Point 2Y | 16#275A = 10074 | 16#2046/4B | 16#93/01/4B = 147/01/75 |  | Configuration and settings | R/WS | INT (Signed16) | 0.1 A | 0.0 A | -3276.7 A ... 3276.7 A | [Point 2Y] (CP2) | [EXTERNAL WEIGHT MEAS.] (ELM)
CTV | Catalogue version | 16#3A8F = 14991 | 16#2077/5C | 16#AB/01/C0 = 171/01/192 |  | Function blocks | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Catalogue version] (CTV) | [FB IDENTIFICATION] (FBI) [FB IDENTIFICATION] (FBI)
DAL | Slowdown limit config. | 16#30DD = 12509 | 16#205F/A | 16#9F/01/6E = 159/01/110 | L_H | Configuration and settings | R/WS | WORD (Enumeration) | - | [Active low] LO |  | [Slowdown limit cfg.] (DAL) | [POSITIONING BY SENSORS] (LPO)
DANF | Available ANF detection direction | 16#160B = 5643 | 16#201A/2C | 16#7D/01/2C = 125/01/44 | DANF | Configuration and settings | R/WS | WORD (Enumeration) | - | [Trip in case of overspeed] OVER |  | [ANF Direction check] (DANF) | [ENCODER CONFIGURATION] (IEN) [ENCODER FAULT] (SDD)
DAS | Delay to open contactor | 16#332E = 13102 | 16#2065/3 | 16#A2/01/67 = 162/01/103 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.10 s | 0.00 s ... 5.00 s | [Delay to open cont.] (DAS) | [OUTPUT CONTACTOR CMD] (OCC)
DBS | Delay to close o/p cont. | 16#332D = 13101 | 16#2065/2 | 16#A2/01/66 = 162/01/102 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.15 s | 0.05 s ... 60.00 s | [Delay to motor run] (DBS) | [OUTPUT CONTACTOR CMD] (OCC)
DCCC | DC Bus compatibility | 16#361B = 13851 | 16#206C/34 | 16#A6/01/34 = 166/01/52 | DCCC | Configuration and settings | R/WS | WORD (Enumeration) | - | [Altivar compatibility] ATV |  | [DC-Bus compat.] (DCCC) | [DC Bus] (DCC)
DCCM | DC Bus chaining mode | 16#361A = 13850 | 16#206C/33 | 16#A6/01/33 = 166/01/51 | DCCM | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [DC-Bus chaining] (DCCM) | [DC Bus] (DCC)
DTF | Decrease ref. speed | 16#2FB3 = 12211 | 16#205C/C | 16#9E/01/0C = 158/01/12 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Decrease ref. speed] (DTF) | [TRAVERSE CONTROL] (TR0)
EBHT | Encoder board HW type | 16#0DE9 = 3561 | 16#2005/3E | 16#72/01/A2 = 114/01/162 | EBHT | Configuration and settings | R | WORD (Enumeration) | - | [Not configured] NO
EBO | End of reel | 16#2FB5 = 12213 | 16#205C/E | 16#9E/01/0E = 158/01/14 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [End reel] (EBO) | [TRAVERSE CONTROL] (TR0)
ETHM | Ethernet protocol | 16#FAF1 = 64241 |  |  | ETHM | Configuration and settings | R/W | WORD (Enumeration) | - | [ModbusTCP] MBTP |  | [Ethernet protocol] (ETHM) | [COMMUNICATION CARD] (CBD)
FANF | Detection frequency of ANF detected fault | 16#160A = 5642 | 16#201A/2B | 16#7D/01/2B = 125/01/43 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 5.0 Hz | 0.1 Hz ... 50.0 Hz | [ANF Frequency Thd.] (FANF) | [ENCODER CONFIGURATION] (IEN) [ENCODER FAULT] (SDD)
FBCD | FB command | 16#3A72 = 14962 | 16#2077/3F | 16#AB/01/A3 = 171/01/163 | SPST | Function blocks | R/W | WORD (Enumeration) | - |  |  | [FB command] (FBCD) | [FUNCTION BLOCKS] (FBM)
FBDF | FB behaviour on drive fault | 16#3A75 = 14965 | 16#2077/42 | 16#AB/01/A6 = 171/01/166 | SPIG | Function blocks | R/WS | WORD (Enumeration) | - | [Stop] STOP |  | [FB on drive fault] (FBDF) | [FUNCTION BLOCKS] (FBM)
FBFT | FB fault | 16#3A71 = 14961 | 16#2077/3E | 16#AB/01/A2 = 171/01/162 | FBFT | Function blocks | R | WORD (Enumeration) | - |  |  | [FB fault] (FBFT) | [MONIT. FUN. BLOCKS] (MFB) [MONIT. FUN. BLOCKS] (MFB)
FBRM | FB start mode | 16#3A73 = 14963 | 16#2077/40 | 16#AB/01/A4 = 171/01/164 | PSLIN | Function blocks | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [FB start mode] (FBRM) | [FUNCTION BLOCKS] (FBM)
FBSM | Stop of FB stops the motor | 16#3A74 = 14964 | 16#2077/41 | 16#AB/01/A5 = 171/01/165 | ECFG | Function blocks | R/WS | WORD (Enumeration) | - | [Freewheel stop on fault] YES |  | [Stop FB stop motor] (FBSM) | [FUNCTION BLOCKS] (FBM)
FBST | FB status | 16#3A70 = 14960 | 16#2077/3D | 16#AB/01/A1 = 171/01/161 | FBST | Function blocks | R | WORD (Enumeration) | - |  |  | [FB status] (FBST) | [MONIT. FUN. BLOCKS] (MFB) [MONIT. FUN. BLOCKS] (MFB)
FDRD | Ethernet : FDR fault | 16#FAE9 = 64233 |  |  |  | Fault parameters | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [FDR fault] (FDRD) | [COMMUNICATION CARD] (CBD)
GDLA | Guard Door Locking assignment | 16#3C1E = 15390 | 16#207B/5B | 16#AD/01/BF = 173/01/191 | SMSA | Safety function | R/WS | WORD (Enumeration) | - | [None] NO
GDLS | GDL Status | 16#3C21 = 15393 | 16#207B/5E | 16#AD/01/C2 = 173/01/194 | GDLS | Safety function | R | WORD (Enumeration) | - |  |  | [None] (GDLS) | [MONIT. SAFETY] (SAF)
GLB | Global transmit | 16#19CF = 6607 | 16#2024/8 | 16#82/01/08 = 130/01/08 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 32
GLLD | GDL Long delay | 16#3C1F = 15391 | 16#207B/5C | 16#AD/01/C0 = 173/01/192 |  | Safety function | R/WS | UINT (Unsigned16) | 1 s | 1 s | 1 s ... 3600 s
GLSD | GDL Short delay | 16#3C20 = 15392 | 16#207B/5D | 16#AD/01/C1 = 173/01/193 |  | Safety function | R/WS | UINT (Unsigned16) | 1 s | 1 s | 1 s ... 3600 s
HRFC | Hard reset fault configuration | 16#1BEE = 7150 | 16#2029/33 | 16#84/01/97 = 132/01/151 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [None] (HRFC) | [FAULT RESET] (RST)
I2TA | I2t model activation for current limitation | 16#259F = 9631 | 16#2042/20 | 16#91/01/20 = 145/01/32 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [I2t model activation] (I2TA) | [Dyn Current limit] (I2T)
I2TI | maximum current of I2t model | 16#25A0 = 9632 | 16#2042/21 | 16#91/01/21 = 145/01/33 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 A | Refer to programming manual | 0.0 A ... 6553.5 A | [max current of I2t] (I2TI) | [Dyn Current limit] (I2T)
I2TM | Monitoring of I2t overload level | 16#25A2 = 9634 | 16#2042/23 | 16#91/01/23 = 145/01/35 |  | Configuration and settings | R | UINT (Unsigned16) | 1 % |  | 0 % ... 100 % | [I2t overload level] (I2TM) | [MONIT. MOTOR] (MMO)
I2TT | maximum time of I2t model | 16#25A1 = 9633 | 16#2042/22 | 16#91/01/22 = 145/01/34 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 655.35 s | [max time of I2t] (I2TT) | [Dyn Current limit] (I2T)
IA01 | FB : Analog Input XX assignment | 16#3A34 = 14900 | 16#2077/1 | 16#AB/01/65 = 171/01/101 | PSA | Function blocks | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [None] (IA01) | [INPUTS ASSIGNMENTS] (FBA)
IA02 | FB : Analog Input XX assignment | 16#3A35 = 14901 | 16#2077/2 | 16#AB/01/66 = 171/01/102 | PSA | Function blocks | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [None] (IA02) | [INPUTS ASSIGNMENTS] (FBA)
IA03 | FB : Analog Input XX assignment | 16#3A36 = 14902 | 16#2077/3 | 16#AB/01/67 = 171/01/103 | PSA | Function blocks | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [None] (IA03) | [INPUTS ASSIGNMENTS] (FBA)
IA04 | FB : Analog Input XX assignment | 16#3A37 = 14903 | 16#2077/4 | 16#AB/01/68 = 171/01/104 | PSA | Function blocks | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [None] (IA04) | [INPUTS ASSIGNMENTS] (FBA)
IA05 | FB : Analog Input XX assignment | 16#3A38 = 14904 | 16#2077/5 | 16#AB/01/69 = 171/01/105 | PSA | Function blocks | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [None] (IA05) | [INPUTS ASSIGNMENTS] (FBA)
IA06 | FB : Analog Input XX assignment | 16#3A39 = 14905 | 16#2077/6 | 16#AB/01/6A = 171/01/106 | PSA | Function blocks | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [None] (IA06) | [INPUTS ASSIGNMENTS] (FBA)
IA07 | FB : Analog Input XX assignment | 16#3A3A = 14906 | 16#2077/7 | 16#AB/01/6B = 171/01/107 | PSA | Function blocks | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [None] (IA07) | [INPUTS ASSIGNMENTS] (FBA)
IA08 | FB : Analog Input XX assignment | 16#3A3B = 14907 | 16#2077/8 | 16#AB/01/6C = 171/01/108 | PSA | Function blocks | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [None] (IA08) | [INPUTS ASSIGNMENTS] (FBA)
IA09 | FB : Analog Input XX assignment | 16#3A3C = 14908 | 16#2077/9 | 16#AB/01/6D = 171/01/109 | PSA | Function blocks | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [None] (IA09) | [INPUTS ASSIGNMENTS] (FBA)
IA10 | FB : Analog Input XX assignment | 16#3A3D = 14909 | 16#2077/A | 16#AB/01/6E = 171/01/110 | PSA | Function blocks | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [None] (IA10) | [INPUTS ASSIGNMENTS] (FBA)
IBRA | IBR when weight loss | 16#275B = 10075 | 16#2046/4C | 16#93/01/4C = 147/01/76 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | 0.0 A | 0.0 A ... 6553.5 A | [Ibr 4-20 mA loss] (IBRA) | [EXTERNAL WEIGHT MEAS.] (ELM)
ICFG | Selection of local or server configuration | 16#FB14 = 64276 |  |  | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [No] NO |  | [iPar Local Conf] (ICFG) | [COMMUNICATION CARD] (CBD)
IL01 | FB : Logical Input XX assignment | 16#3A48 = 14920 | 16#2077/15 | 16#AB/01/79 = 171/01/121 | PSL | Function blocks | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [None] (IL01) | [INPUTS ASSIGNMENTS] (FBA)
IL02 | FB : Logical Input XX assignment | 16#3A49 = 14921 | 16#2077/16 | 16#AB/01/7A = 171/01/122 | PSL | Function blocks | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [None] (IL02) | [INPUTS ASSIGNMENTS] (FBA)
IL03 | FB : Logical Input XX assignment | 16#3A4A = 14922 | 16#2077/17 | 16#AB/01/7B = 171/01/123 | PSL | Function blocks | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [None] (IL03) | [INPUTS ASSIGNMENTS] (FBA)
IL04 | FB : Logical Input XX assignment | 16#3A4B = 14923 | 16#2077/18 | 16#AB/01/7C = 171/01/124 | PSL | Function blocks | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [None] (IL04) | [INPUTS ASSIGNMENTS] (FBA)
IL05 | FB : Logical Input XX assignment | 16#3A4C = 14924 | 16#2077/19 | 16#AB/01/7D = 171/01/125 | PSL | Function blocks | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [None] (IL05) | [INPUTS ASSIGNMENTS] (FBA)
IL06 | FB : Logical Input XX assignment | 16#3A4D = 14925 | 16#2077/1A | 16#AB/01/7E = 171/01/126 | PSL | Function blocks | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [None] (IL06) | [INPUTS ASSIGNMENTS] (FBA)
IL07 | FB : Logical Input XX assignment | 16#3A4E = 14926 | 16#2077/1B | 16#AB/01/7F = 171/01/127 | PSL | Function blocks | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [None] (IL07) | [INPUTS ASSIGNMENTS] (FBA)
IL08 | FB : Logical Input XX assignment | 16#3A4F = 14927 | 16#2077/1C | 16#AB/01/80 = 171/01/128 | PSL | Function blocks | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [None] (IL08) | [INPUTS ASSIGNMENTS] (FBA)
IL09 | FB : Logical Input XX assignment | 16#3A50 = 14928 | 16#2077/1D | 16#AB/01/81 = 171/01/129 | PSL | Function blocks | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [None] (IL09) | [INPUTS ASSIGNMENTS] (FBA)
IL10 | FB : Logical Input XX assignment | 16#3A51 = 14929 | 16#2077/1E | 16#AB/01/82 = 171/01/130 | PSL | Function blocks | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [None] (IL10) | [INPUTS ASSIGNMENTS] (FBA)
IPAE | iPar service status | 16#FB17 = 64279 |  |  | IPAE | Configuration and settings | R/W | WORD (Enumeration) | - | [idle state] IDLE |  | [iPar State] (IPAE) | [COMMUNICATION CARD] (CBD)
IPAF | iPar detected fault management activation | 16#FB15 = 64277 |  |  | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [Yes] YES |  | [iPar Error Mgt] (IPAF) | [COMMUNICATION CARD] (CBD)
IPAS | iPar autosave service activation | 16#FB13 = 64275 |  |  | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [No] NO |  | [iPar Autosave] (IPAS) | [COMMUNICATION CARD] (CBD)
IPAT | Interval for periodic saving of the iPar service | 16#FB16 = 64278 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 10 | 0 ... 9999 | [iPar timer] (IPAT) | [COMMUNICATION CARD] (CBD)
IPAV | iPar service activation | 16#FB12 = 64274 |  |  | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [No] NO |  | [iPar Validation] (IPAV) | [COMMUNICATION CARD] (CBD)
IPM | IP mode | 16#FAFA = 64250 |  |  | IPM | Configuration and settings | R/W | WORD (Enumeration) | - | Refer to programming manual |  | [IP mode] (IPM) | [COMMUNICATION CARD] (CBD)
LA01 | FB : ADL Container XX | 16#3A5C = 14940 | 16#2077/29 | 16#AB/01/8D = 171/01/141 |  | Function blocks | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
LA02 | FB : ADL Container XX | 16#3A5D = 14941 | 16#2077/2A | 16#AB/01/8E = 171/01/142 |  | Function blocks | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
LA03 | FB : ADL Container XX | 16#3A5E = 14942 | 16#2077/2B | 16#AB/01/8F = 171/01/143 |  | Function blocks | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
LA04 | FB : ADL Container XX | 16#3A5F = 14943 | 16#2077/2C | 16#AB/01/90 = 171/01/144 |  | Function blocks | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
LA05 | FB : ADL Container XX | 16#3A60 = 14944 | 16#2077/2D | 16#AB/01/91 = 171/01/145 |  | Function blocks | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
LA06 | FB : ADL Container XX | 16#3A61 = 14945 | 16#2077/2E | 16#AB/01/92 = 171/01/146 |  | Function blocks | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
LA07 | FB : ADL Container XX | 16#3A62 = 14946 | 16#2077/2F | 16#AB/01/93 = 171/01/147 |  | Function blocks | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
LA08 | FB : ADL Container XX | 16#3A63 = 14947 | 16#2077/30 | 16#AB/01/94 = 171/01/148 |  | Function blocks | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
LA1D | LA1 On Delay | 16#0FB5 = 4021 | 16#200A/16 | 16#75/01/16 = 117/01/22 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 200 ms | [LA1 On Delay] (LA1D) | [LA1 assignment] (LA1A) [LA1 CONFIGURATION] (LA1)
LA2D | LA2 On Delay | 16#0FB6 = 4022 | 16#200A/17 | 16#75/01/17 = 117/01/23 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 200 ms | [LA2 On Delay] (LA2D) | [LA2 assignment] (LA2A) [LA2 CONFIGURATION] (LA2)
LANF | Detection level of ANF detected fault | 16#1608 = 5640 | 16#201A/29 | 16#7D/01/29 = 125/01/41 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 10.0 Hz | [ANF Detection level] (LANF) | [ENCODER CONFIGURATION] (IEN) [ENCODER FAULT] (SDD)
LET | External fault config | 16#1BB2 = 7090 | 16#2028/5B | 16#84/01/5B = 132/01/91 | L_H | Configuration and settings | R/WS | WORD (Enumeration) | - | [Active high] HIG |  | [External fault config] (LET) | [EXTERNAL FAULT] (ETF)
LIDT | LI Debounce Time | 16#3BE2 = 15330 | 16#207B/1F | 16#AD/01/83 = 173/01/131 |  | Safety function | R/WS | UINT (Unsigned16) | 1 ms | 50 ms | 0 ms ... 2000 ms
LIRT | LI Response Time | 16#3BE3 = 15331 | 16#207B/20 | 16#AD/01/84 = 173/01/132 |  | Safety function | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 50 ms
LO1 | LO1 assignment | 16#1391 = 5009 | 16#2014/A | 16#7A/01/0A = 122/01/10 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [LO1 assignment] (LO1) | [LO1 CONFIGURATION] (LO1)
LO1D | LO1 delay time | 16#1099 = 4249 | 16#200C/32 | 16#76/01/32 = 118/01/50 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [LO1 delay time] (LO1D) | [LO1 CONFIGURATION] (LO1)
LO1H | LO1 holding time | 16#1085 = 4229 | 16#200C/1E | 16#76/01/1E = 118/01/30 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [LO1 holding time] (LO1H) | [LO1 CONFIGURATION] (LO1)
LO1S | LO1 active level | 16#1071 = 4209 | 16#200C/A | 16#76/01/0A = 118/01/10 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [LO1 active at] (LO1S) | [LO1 CONFIGURATION] (LO1)
LO1F | Enable DQ1 fallback | 16#10C4 = 4292 | 16#200C/5D | 16#76/01/5D = 118/01/93 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Enable DQ1 fallback] (LO1F) | [LO1 CONFIGURATION] (LO1)
LP1 | Ext weight point 1 X | 16#2757 = 10071 | 16#2046/48 | 16#93/01/48 = 147/01/72 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 % | 0.00 % | 0.00 % ... 99.99 % | [Point 1 X] (LP1) | [EXTERNAL WEIGHT MEAS.] (ELM)
LP2 | Ext weight point 2 X | 16#2759 = 10073 | 16#2046/4A | 16#93/01/4A = 147/01/74 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 % | 50.00 % | 0.01 % ... 100.00 % | [Point 2 X] (LP2) | [EXTERNAL WEIGHT MEAS.] (ELM)
LRS1 | Logic result status 1 (PSL 000-015) | 16#0CB2 = 3250 | 16#2002/33 | 16#71/01/33 = 113/01/51 |  | Status parameters | R | WORD (BitString16) | -
LRS2 | Logic result status 2 (PSL 016-031) | 16#0CB3 = 3251 | 16#2002/34 | 16#71/01/34 = 113/01/52 |  | Status parameters | R | WORD (BitString16) | -
LRS3 | Logic result status 3 (PSL 032-047) | 16#0CB4 = 3252 | 16#2002/35 | 16#71/01/35 = 113/01/53 |  | Status parameters | R | WORD (BitString16) | -
LRS4 | Logic result status 4 (PSL 048-063) | 16#0CB5 = 3253 | 16#2002/36 | 16#71/01/36 = 113/01/54 |  | Status parameters | R | WORD (BitString16) | -
LRS5 | Logic result status 5 (PSL 064-079) | 16#0CB6 = 3254 | 16#2002/37 | 16#71/01/37 = 113/01/55 |  | Status parameters | R | WORD (BitString16) | -
LRS6 | Logic result status 6 (PSL 080-095) | 16#0CB7 = 3255 | 16#2002/38 | 16#71/01/38 = 113/01/56 |  | Status parameters | R | WORD (BitString16) | -
LRS7 | Logic result status 7 (PSL 096-111) | 16#0CB8 = 3256 | 16#2002/39 | 16#71/01/39 = 113/01/57 |  | Status parameters | R | WORD (BitString16) | -
LRS8 | Logic result status 8 (PSL 112-127) | 16#0CB9 = 3257 | 16#2002/3A | 16#71/01/3A = 113/01/58 |  | Status parameters | R | WORD (BitString16) | -
M001 | FB : M0XX parameter | 16#3A7A = 14970 | 16#2077/47 | 16#AB/01/AB = 171/01/171 |  | Function blocks | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (M001) | [FB PARAMETERS] (FBP)
M002 | FB : M0XX parameter | 16#3A7B = 14971 | 16#2077/48 | 16#AB/01/AC = 171/01/172 |  | Function blocks | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (M002) | [FB PARAMETERS] (FBP)
M003 | FB : M0XX parameter | 16#3A7C = 14972 | 16#2077/49 | 16#AB/01/AD = 171/01/173 |  | Function blocks | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (M003) | [FB PARAMETERS] (FBP)
M004 | FB : M0XX parameter | 16#3A7D = 14973 | 16#2077/4A | 16#AB/01/AE = 171/01/174 |  | Function blocks | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (M004) | [FB PARAMETERS] (FBP)
M005 | FB : M0XX parameter | 16#3A7E = 14974 | 16#2077/4B | 16#AB/01/AF = 171/01/175 |  | Function blocks | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (M005) | [FB PARAMETERS] (FBP)
M006 | FB : M0XX parameter | 16#3A7F = 14975 | 16#2077/4C | 16#AB/01/B0 = 171/01/176 |  | Function blocks | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (M006) | [FB PARAMETERS] (FBP)
M007 | FB : M0XX parameter | 16#3A80 = 14976 | 16#2077/4D | 16#AB/01/B1 = 171/01/177 |  | Function blocks | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (M007) | [FB PARAMETERS] (FBP)
M008 | FB : M0XX parameter | 16#3A81 = 14977 | 16#2077/4E | 16#AB/01/B2 = 171/01/178 |  | Function blocks | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (M008) | [FB PARAMETERS] (FBP)
NTJ | IGBT alarm Nb | 16#0CA9 = 3241 | 16#2002/2A | 16#71/01/2A = 113/01/42 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [IGBT alarm Nb] (NTJ) | [DIAGNOSTICS] (DGT)
OCC | Output contactor control | 16#3330 = 13104 | 16#2065/5 | 16#A2/01/69 = 162/01/105 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [Out. contactor ass.] (OCC) | [OUTPUT CONTACTOR CMD] (OCC)
PES | Weight sensor assignt | 16#2756 = 10070 | 16#2046/47 | 16#93/01/47 = 147/01/71 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Weight sensor ass.] (PES) | [EXTERNAL WEIGHT MEAS.] (ELM)
PFI | RP filter | 16#33F8 = 13304 | 16#2067/5 | 16#A3/01/69 = 163/01/105 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 1000 ms | [RP filter] (PFI) | [RP input] (PFRC) [LI5 CONFIGURATION] (L5)
PFR | RP maximum value | 16#33F7 = 13303 | 16#2067/4 | 16#A3/01/68 = 163/01/104 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 kHz | 20.00 kHz | 0.00 kHz ... 20.00 kHz | [RP max value] (PFR) | [RP input] (PFRC) [LI5 CONFIGURATION] (L5)
PIL | Minimum pulse input | 16#33F6 = 13302 | 16#2067/3 | 16#A3/01/67 = 163/01/103 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 kHz | 0.00 kHz | 0.00 kHz ... 20.00 kHz | [RP min value ] (PIL) | [RP input] (PFRC) [LI5 CONFIGURATION] (L5)
PRC | Peer Cop node | 16#19CE = 6606 | 16#2024/7 | 16#82/01/07 = 130/01/07 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO
PTCL | LI6 = PTC probe | 16#3393 = 13203 | 16#2066/4 | 16#A3/01/04 = 163/01/04 | PTCX | Configuration and settings | R/WS | WORD (Enumeration) | - | [No management] NO |  | [LI6 = PTC probe] (PTCL) | [PTC MANAGEMENT] (PTC)
PWRM | PWRM Assignment | 16#3BD9 = 15321 | 16#207B/16 | 16#AD/01/7A = 173/01/122 | SPSL | Safety function | R/WS | WORD (Enumeration) | - | [None] PWRM
QSH | Quick step high | 16#2FAC = 12204 | 16#205C/5 | 16#9E/01/05 = 158/01/05 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 10.0 Hz | [Quick step High] (QSH) | [SETTINGS] (SET) [TRAVERSE CONTROL] (TR0)
QSL | Quick step low | 16#2FAD = 12205 | 16#205C/6 | 16#9E/01/06 = 158/01/06 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 10.0 Hz | [Quick step Low] (QSL) | [SETTINGS] (SET) [TRAVERSE CONTROL] (TR0)
R1F | R1 FallBack Enable | 16#10C2 = 4290 | 16#200C/5B | 16#76/01/5B = 118/01/91 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [None] (R1F) | [R1 CONFIGURATION] (R1)
R2F | R2 FallBack Enable | 16#10C3 = 4291 | 16#200C/5C | 16#76/01/5C = 118/01/92 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [None] (R2F) | [R2 CONFIGURATION] (R2)
RCA | Output contactor fdbk | 16#332F = 13103 | 16#2065/4 | 16#A2/01/68 = 162/01/104 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Output contact. fdbk] (RCA) | [OUTPUT CONTACTOR CMD] (OCC)
RSL | PID wake up threshold | 16#2EB8 = 11960 | 16#2059/3D | 16#9C/01/A1 = 156/01/161 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 | 0.0 | 0.0 ... 100.0 | [PID wake up thresh.] (RSL) | [PID REGULATOR] (PID)
RTR | Traverse control reset | 16#2FB2 = 12210 | 16#205C/B | 16#9E/01/0B = 158/01/11 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Init. traverse ctrl] (RTR) | [TRAVERSE CONTROL] (TR0)
S001 | FB system word 01 | 16#3A84 = 14980 | 16#2077/51 | 16#AB/01/B5 = 171/01/181 |  | Function blocks | R | WORD (BitString16) | -
S002 | FB system word 02 | 16#3A85 = 14981 | 16#2077/52 | 16#AB/01/B6 = 171/01/182 |  | Function blocks | R | WORD (BitString16) | -
S006 | FB system word 06 | 16#3A89 = 14985 | 16#2077/56 | 16#AB/01/BA = 171/01/186 |  | Function blocks | R | WORD (BitString16) | -
SAF1 | Safety fault register 1 | 16#3BF6 = 15350 | 16#207B/33 | 16#AD/01/97 = 173/01/151 |  | Safety function | R | WORD (BitString16) | - |  |  | [Safety fault Reg1] (SAF1) | [MORE FAULT INFO] (AFI)
SAF2 | Safety fault register 2 | 16#3BFF = 15359 | 16#207B/3C | 16#AD/01/A0 = 173/01/160 |  | Safety function | R | WORD (BitString16) | - |  |  | [Safety fault Reg2] (SAF2) | [MORE FAULT INFO] (AFI)
SAL | Stop limit configuration | 16#30DC = 12508 | 16#205F/9 | 16#9F/01/6D = 159/01/109 | L_H | Configuration and settings | R/WS | WORD (Enumeration) | - | [Active low] LO |  | [Stop limit config.] (SAL) | [POSITIONING BY SENSORS] (LPO)
SAT | Thermal alarm stop | 16#2B0D = 11021 | 16#2050/16 | 16#98/01/16 = 152/01/22 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Thermal alarm stop] (SAT) | [THERMAL ALARM STOP] (SAT)
SCL3 | Ground short circuit detection | 16#1B6A = 7018 | 16#2028/13 | 16#84/01/13 = 132/01/19 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Ground short circuit] (SCL3) | [DC Bus] (DCC)
SDS | Customer scale factor | 16#2EE1 = 12001 | 16#205A/2 | 16#9D/01/02 = 157/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 | 30.0 | 0.1 ... 200.0 | [Scale factor display] (SDS) | [SETTINGS] (SET)
SF00 | Safety fault subregister 0 | 16#3BF7 = 15351 | 16#207B/34 | 16#AD/01/98 = 173/01/152 |  | Safety function | R | WORD (BitString16) | - |  |  | [SAFF Subcode 0] (SF00) | [MORE FAULT INFO] (AFI)
SF01 | Safety fault subregister 1 | 16#3BF8 = 15352 | 16#207B/35 | 16#AD/01/99 = 173/01/153 |  | Safety function | R | WORD (BitString16) | - |  |  | [SAFF Subcode 1] (SF01) | [MORE FAULT INFO] (AFI)
SF02 | Safety fault subregister 2 | 16#3BF9 = 15353 | 16#207B/36 | 16#AD/01/9A = 173/01/154 |  | Safety function | R | WORD (BitString16) | - |  |  | [SAFF Subcode 2] (SF02) | [MORE FAULT INFO] (AFI)
SF03 | Safety fault subregister 3 | 16#3BFA = 15354 | 16#207B/37 | 16#AD/01/9B = 173/01/155 |  | Safety function | R | WORD (BitString16) | - |  |  | [SAFF Subcode 3] (SF03) | [MORE FAULT INFO] (AFI)
SF04 | Safety fault subregister 4 | 16#3BFB = 15355 | 16#207B/38 | 16#AD/01/9C = 173/01/156 |  | Safety function | R | WORD (BitString16) | - |  |  | [SAFF Subcode 4] (SF04) | [MORE FAULT INFO] (AFI)
SF05 | Safety fault subregister 5 | 16#3BFC = 15356 | 16#207B/39 | 16#AD/01/9D = 173/01/157 |  | Safety function | R | WORD (BitString16) | - |  |  | [SAFF Subcode 5] (SF05) | [MORE FAULT INFO] (AFI)
SF06 | Safety fault subregister 6 | 16#3BFD = 15357 | 16#207B/3A | 16#AD/01/9E = 173/01/158 |  | Safety function | R | WORD (BitString16) | - |  |  | [SAFF Subcode 6] (SF06) | [MORE FAULT INFO] (AFI)
SF07 | Safety fault subregister 7 | 16#3BFE = 15358 | 16#207B/3B | 16#AD/01/9F = 173/01/159 |  | Safety function | R | WORD (BitString16) | - |  |  | [SAFF Subcode 7] (SF07) | [MORE FAULT INFO] (AFI)
SF08 | Safety fault subregister 8 | 16#3C00 = 15360 | 16#207B/3D | 16#AD/01/A1 = 173/01/161 |  | Safety function | R | WORD (BitString16) | - |  |  | [SAFF Subcode 8] (SF08) | [MORE FAULT INFO] (AFI)
SF09 | Safety fault subregister 9 | 16#3C01 = 15361 | 16#207B/3E | 16#AD/01/A2 = 173/01/162 |  | Safety function | R | WORD (BitString16) | - |  |  | [SAFF Subcode 9] (SF09) | [MORE FAULT INFO] (AFI)
SF10 | Safety fault subregister 10 | 16#3C02 = 15362 | 16#207B/3F | 16#AD/01/A3 = 173/01/163 |  | Safety function | R | WORD (BitString16) | - |  |  | [SAFF Subcode 10] (SF10) | [MORE FAULT INFO] (AFI)
SF11 | Safety fault subregister 11 | 16#3C03 = 15363 | 16#207B/40 | 16#AD/01/A4 = 173/01/164 |  | Safety function | R | WORD (BitString16) | - |  |  | [SAFF Subcode 11] (SF11) | [MORE FAULT INFO] (AFI)
SFTY | Drive Safety status | 16#3BF0 = 15344 | 16#207B/2D | 16#AD/01/91 = 173/01/145 | SFTY | Safety function | R | WORD (Enumeration) | -
SLSA | SLS Assignment | 16#3BC4 = 15300 | 16#207B/1 | 16#AD/01/65 = 173/01/101 | SPSL | Safety function | R/WS | WORD (Enumeration) | - | [None] NO
SLSP | SLS Set Point | 16#3BC6 = 15302 | 16#207B/3 | 16#AD/01/67 = 173/01/103 |  | Safety function | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz
SLSS | Safe limited speed status | 16#3BC8 = 15304 | 16#207B/5 | 16#AD/01/69 = 173/01/105 | SLSS | Safety function | R | WORD (Enumeration) | - |  |  | [SLS status] (SLSS) | [MONIT. SAFETY] (SAF)
SLT | SLS Type | 16#3BC5 = 15301 | 16#207B/2 | 16#AD/01/66 = 173/01/102 | SLT | Safety function | R/WS | WORD (Enumeration) | - | [None] TYP1
SLTT | SLS Tolerance Threshold | 16#3BC7 = 15303 | 16#207B/4 | 16#AD/01/68 = 173/01/104 |  | Safety function | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz
SLWT | SLS Wait Time | 16#3BC9 = 15305 | 16#207B/6 | 16#AD/01/6A = 173/01/106 |  | Safety function | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 5000 ms
SMLH | SMS Speed High Limit | 16#3C16 = 15382 | 16#207B/53 | 16#AD/01/B7 = 173/01/183 |  | Safety function | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 6553.5 Hz
SMLL | SMS Speed Low Limit | 16#3C15 = 15381 | 16#207B/52 | 16#AD/01/B6 = 173/01/182 |  | Safety function | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 6553.5 Hz
SMLS | SMS Speed Selection | 16#3C17 = 15383 | 16#207B/54 | 16#AD/01/B8 = 173/01/184 | SPSL | Safety function | R/WS | WORD (Enumeration) | - | [None] NO
SMSA | Safely speed limiteed assignment | 16#3C14 = 15380 | 16#207B/51 | 16#AD/01/B5 = 173/01/181 | SMSA | Safety function | R/WS | WORD (Enumeration) | - | [None] NO
SMSS | SMS Status | 16#3C18 = 15384 | 16#207B/55 | 16#AD/01/B9 = 173/01/185 | SMSS | Safety function | R | WORD (Enumeration) | - |  |  | [None] (SMSS) | [MONIT. SAFETY] (SAF)
SNC | Counter wobble | 16#2FB4 = 12212 | 16#205C/D | 16#9E/01/0D = 158/01/13 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Counter wobble] (SNC) | [TRAVERSE CONTROL] (TR0)
SPD2 | Output value Customer | 16#2EE9 = 12009 | 16#205A/A | 16#9D/01/0A = 157/01/10 |  | Configuration and settings | R | UINT (Unsigned16) | 0.1 |  | 0.0 ... 6553.5 | [Cust. output value] (SPD2) | [MONITORING] (MON)
SPD3 | Output value Customer | 16#2EEA = 12010 | 16#205A/B | 16#9D/01/0B = 157/01/11 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Cust. output value ] (SPD3) | [MONITORING] (MON)
SPDT | DRIVECOM : Deceleration - Time delta | 16#21A8 = 8616 | 16#2038/11 | 16#8C/01/11 = 140/01/17 |  | CiA 402 settings | R/W | UINT (Unsigned16) | 1 s |  | 0 s ... 65535 s
SR11 | SAF1 REGISTER x (1 is last) | 16#1CE9 = 7401 | 16#202C/2 | 16#86/01/02 = 134/01/02 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Saf1 Reg n-1] (SR11) | [None] (DP1)
SR12 | SAF1 REGISTER x (1 is last) | 16#1CEA = 7402 | 16#202C/3 | 16#86/01/03 = 134/01/03 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Saf1 Reg n-2] (SR12) | [None] (DP2)
SR13 | SAF1 REGISTER x (1 is last) | 16#1CEB = 7403 | 16#202C/4 | 16#86/01/04 = 134/01/04 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Saf1 Reg n-3] (SR13) | [None] (DP3)
SR14 | SAF1 REGISTER x (1 is last) | 16#1CEC = 7404 | 16#202C/5 | 16#86/01/05 = 134/01/05 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Saf1 Reg n-4] (SR14) | [None] (DP4)
SR15 | SAF1 REGISTER x (1 is last) | 16#1CED = 7405 | 16#202C/6 | 16#86/01/06 = 134/01/06 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Saf1 Reg n-5] (SR15) | [None] (DP5)
SR16 | SAF1 REGISTER x (1 is last) | 16#1CEE = 7406 | 16#202C/7 | 16#86/01/07 = 134/01/07 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Saf1 Reg n-6] (SR16) | [None] (DP6)
SR17 | SAF1 REGISTER x (1 is last) | 16#1CEF = 7407 | 16#202C/8 | 16#86/01/08 = 134/01/08 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Saf1 Reg n-7] (SR17) | [None] (DP7)
SR18 | SAF1 REGISTER x (1 is last) | 16#1CF0 = 7408 | 16#202C/9 | 16#86/01/09 = 134/01/09 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Saf1 Reg n-8] (SR18) | [None] (DP8)
SR21 | SAF2 REGISTER x (1 is last) | 16#1CF3 = 7411 | 16#202C/C | 16#86/01/0C = 134/01/12 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Saf2 Reg n-1] (SR21) | [None] (DP1)
SR22 | SAF2 REGISTER x (1 is last) | 16#1CF4 = 7412 | 16#202C/D | 16#86/01/0D = 134/01/13 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Saf2 Reg n-2] (SR22) | [None] (DP2)
SR23 | SAF2 REGISTER x (1 is last) | 16#1CF5 = 7413 | 16#202C/E | 16#86/01/0E = 134/01/14 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Saf2 Reg n-3] (SR23) | [None] (DP3)
SR24 | SAF2 REGISTER x (1 is last) | 16#1CF6 = 7414 | 16#202C/F | 16#86/01/0F = 134/01/15 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Saf2 Reg n-4] (SR24) | [None] (DP4)
SR25 | SAF2 REGISTER x (1 is last) | 16#1CF7 = 7415 | 16#202C/10 | 16#86/01/10 = 134/01/16 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Saf2 Reg n-5] (SR25) | [None] (DP5)
SR26 | SAF2 REGISTER x (1 is last) | 16#1CF8 = 7416 | 16#202C/11 | 16#86/01/11 = 134/01/17 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Saf2 Reg n-6] (SR26) | [None] (DP6)
SR27 | SAF2 REGISTER x (1 is last) | 16#1CF9 = 7417 | 16#202C/12 | 16#86/01/12 = 134/01/18 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Saf2 Reg n-7] (SR27) | [None] (DP7)
SR28 | SAF2 REGISTER x (1 is last) | 16#1CFA = 7418 | 16#202C/13 | 16#86/01/13 = 134/01/19 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Saf2 Reg n-8] (SR28) | [None] (DP8)
SRA1 | SF00 REGISTER x (1 is last) | 16#1CFD = 7421 | 16#202C/16 | 16#86/01/16 = 134/01/22 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF00 Reg n-1] (SRA1) | [None] (DP1)
SRA2 | SF00 REGISTER x (1 is last) | 16#1CFE = 7422 | 16#202C/17 | 16#86/01/17 = 134/01/23 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF00 Reg n-2] (SRA2) | [None] (DP2)
SRA3 | SF00 REGISTER x (1 is last) | 16#1CFF = 7423 | 16#202C/18 | 16#86/01/18 = 134/01/24 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF00 Reg n-3] (SRA3) | [None] (DP3)
SRA4 | SF00 REGISTER x (1 is last) | 16#1D00 = 7424 | 16#202C/19 | 16#86/01/19 = 134/01/25 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF00 Reg n-4] (SRA4) | [None] (DP4)
SRA5 | SF00 REGISTER x (1 is last) | 16#1D01 = 7425 | 16#202C/1A | 16#86/01/1A = 134/01/26 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF00 Reg n-5] (SRA5) | [None] (DP5)
SRA6 | SF00 REGISTER x (1 is last) | 16#1D02 = 7426 | 16#202C/1B | 16#86/01/1B = 134/01/27 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF00 Reg n-6] (SRA6) | [None] (DP6)
SRA7 | SF00 REGISTER x (1 is last) | 16#1D03 = 7427 | 16#202C/1C | 16#86/01/1C = 134/01/28 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF00 Reg n-7] (SRA7) | [None] (DP7)
SRA8 | SF00 REGISTER x (1 is last) | 16#1D04 = 7428 | 16#202C/1D | 16#86/01/1D = 134/01/29 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF00 Reg n-8] (SRA8) | [None] (DP8)
SRB1 | SF01 REGISTER x (1 is last) | 16#1D07 = 7431 | 16#202C/20 | 16#86/01/20 = 134/01/32 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF01 Reg n-1] (SRB1) | [None] (DP1)
SRB2 | SF01 REGISTER x (1 is last) | 16#1D08 = 7432 | 16#202C/21 | 16#86/01/21 = 134/01/33 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF01 Reg n-2] (SRB2) | [None] (DP2)
SRB3 | SF01 REGISTER x (1 is last) | 16#1D09 = 7433 | 16#202C/22 | 16#86/01/22 = 134/01/34 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF01 Reg n-3] (SRB3) | [None] (DP3)
SRB4 | SF01 REGISTER x (1 is last) | 16#1D0A = 7434 | 16#202C/23 | 16#86/01/23 = 134/01/35 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF01 Reg n-4] (SRB4) | [None] (DP4)
SRB5 | SF01 REGISTER x (1 is last) | 16#1D0B = 7435 | 16#202C/24 | 16#86/01/24 = 134/01/36 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF01 Reg n-5] (SRB5) | [None] (DP5)
SRB6 | SF01 REGISTER x (1 is last) | 16#1D0C = 7436 | 16#202C/25 | 16#86/01/25 = 134/01/37 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF01 Reg n-6] (SRB6) | [None] (DP6)
SRB7 | SF01 REGISTER x (1 is last) | 16#1D0D = 7437 | 16#202C/26 | 16#86/01/26 = 134/01/38 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF01 Reg n-7] (SRB7) | [None] (DP7)
SRB8 | SF01 REGISTER x (1 is last) | 16#1D0E = 7438 | 16#202C/27 | 16#86/01/27 = 134/01/39 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF01 Reg n-8] (SRB8) | [None] (DP8)
SRC1 | SF02 REGISTER x (1 is last) | 16#1D11 = 7441 | 16#202C/2A | 16#86/01/2A = 134/01/42 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF02 Reg n-1] (SRC1) | [None] (DP1)
SRC2 | SF02 REGISTER x (1 is last) | 16#1D12 = 7442 | 16#202C/2B | 16#86/01/2B = 134/01/43 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF02 Reg n-2] (SRC2) | [None] (DP2)
SRC3 | SF02 REGISTER x (1 is last) | 16#1D13 = 7443 | 16#202C/2C | 16#86/01/2C = 134/01/44 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF02 Reg n-3] (SRC3) | [None] (DP3)
SRC4 | SF02 REGISTER x (1 is last) | 16#1D14 = 7444 | 16#202C/2D | 16#86/01/2D = 134/01/45 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF02 Reg n-4] (SRC4) | [None] (DP4)
SRC5 | SF02 REGISTER x (1 is last) | 16#1D15 = 7445 | 16#202C/2E | 16#86/01/2E = 134/01/46 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF02 Reg n-5] (SRC5) | [None] (DP5)
SRC6 | SF02 REGISTER x (1 is last) | 16#1D16 = 7446 | 16#202C/2F | 16#86/01/2F = 134/01/47 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF02 Reg n-6] (SRC6) | [None] (DP6)
SRC7 | SF02 REGISTER x (1 is last) | 16#1D17 = 7447 | 16#202C/30 | 16#86/01/30 = 134/01/48 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF02 Reg n-7] (SRC7) | [None] (DP7)
SRC8 | SF02 REGISTER x (1 is last) | 16#1D18 = 7448 | 16#202C/31 | 16#86/01/31 = 134/01/49 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF02 Reg n-8] (SRC8) | [None] (DP8)
SRD1 | SF03 REGISTER x (1 is last) | 16#1D1B = 7451 | 16#202C/34 | 16#86/01/34 = 134/01/52 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF03 Reg n-1] (SRD1) | [None] (DP1)
SRD2 | SF03 REGISTER x (1 is last) | 16#1D1C = 7452 | 16#202C/35 | 16#86/01/35 = 134/01/53 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF03 Reg n-2] (SRD2) | [None] (DP2)
SRD3 | SF03 REGISTER x (1 is last) | 16#1D1D = 7453 | 16#202C/36 | 16#86/01/36 = 134/01/54 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF03 Reg n-3] (SRD3) | [None] (DP3)
SRD4 | SF03 REGISTER x (1 is last) | 16#1D1E = 7454 | 16#202C/37 | 16#86/01/37 = 134/01/55 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF03 Reg n-4] (SRD4) | [None] (DP4)
SRD5 | SF03 REGISTER x (1 is last) | 16#1D1F = 7455 | 16#202C/38 | 16#86/01/38 = 134/01/56 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF03 Reg n-5] (SRD5) | [None] (DP5)
SRD6 | SF03 REGISTER x (1 is last) | 16#1D20 = 7456 | 16#202C/39 | 16#86/01/39 = 134/01/57 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF03 Reg n-6] (SRD6) | [None] (DP6)
SRD7 | SF03 REGISTER x (1 is last) | 16#1D21 = 7457 | 16#202C/3A | 16#86/01/3A = 134/01/58 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF03 Reg n-7] (SRD7) | [None] (DP7)
SRD8 | SF03 REGISTER x (1 is last) | 16#1D22 = 7458 | 16#202C/3B | 16#86/01/3B = 134/01/59 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF03 Reg n-8] (SRD8) | [None] (DP8)
SRE1 | SF04 REGISTER x (1 is last) | 16#1D25 = 7461 | 16#202C/3E | 16#86/01/3E = 134/01/62 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF04 Reg n-1] (SRE1) | [None] (DP1)
SRE2 | SF04 REGISTER x (1 is last) | 16#1D26 = 7462 | 16#202C/3F | 16#86/01/3F = 134/01/63 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF04 Reg n-2] (SRE2) | [None] (DP2)
SRE3 | SF04 REGISTER x (1 is last) | 16#1D27 = 7463 | 16#202C/40 | 16#86/01/40 = 134/01/64 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF04 Reg n-3] (SRE3) | [None] (DP3)
SRE4 | SF04 REGISTER x (1 is last) | 16#1D28 = 7464 | 16#202C/41 | 16#86/01/41 = 134/01/65 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF04 Reg n-4] (SRE4) | [None] (DP4)
SRE5 | SF04 REGISTER x (1 is last) | 16#1D29 = 7465 | 16#202C/42 | 16#86/01/42 = 134/01/66 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF04 Reg n-5] (SRE5) | [None] (DP5)
SRE6 | SF04 REGISTER x (1 is last) | 16#1D2A = 7466 | 16#202C/43 | 16#86/01/43 = 134/01/67 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF04 Reg n-6] (SRE6) | [None] (DP6)
SRE7 | SF04 REGISTER x (1 is last) | 16#1D2B = 7467 | 16#202C/44 | 16#86/01/44 = 134/01/68 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF04 Reg n-7] (SRE7) | [None] (DP7)
SRE8 | SF04 REGISTER x (1 is last) | 16#1D2C = 7468 | 16#202C/45 | 16#86/01/45 = 134/01/69 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF04 Reg n-8] (SRE8) | [None] (DP8)
SRF1 | SF05 REGISTER x (1 is last) | 16#1D2F = 7471 | 16#202C/48 | 16#86/01/48 = 134/01/72 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF05 Reg n-1] (SRF1) | [None] (DP1)
SRF2 | SF05 REGISTER x (1 is last) | 16#1D30 = 7472 | 16#202C/49 | 16#86/01/49 = 134/01/73 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF05 Reg n-2] (SRF2) | [None] (DP2)
SRF3 | SF05 REGISTER x (1 is last) | 16#1D31 = 7473 | 16#202C/4A | 16#86/01/4A = 134/01/74 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF05 Reg n-3] (SRF3) | [None] (DP3)
SRF4 | SF05 REGISTER x (1 is last) | 16#1D32 = 7474 | 16#202C/4B | 16#86/01/4B = 134/01/75 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF05 Reg n-4] (SRF4) | [None] (DP4)
SRF5 | SF05 REGISTER x (1 is last) | 16#1D33 = 7475 | 16#202C/4C | 16#86/01/4C = 134/01/76 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF05 Reg n-5] (SRF5) | [None] (DP5)
SRF6 | SF05 REGISTER x (1 is last) | 16#1D34 = 7476 | 16#202C/4D | 16#86/01/4D = 134/01/77 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF05 Reg n-6] (SRF6) | [None] (DP6)
SRF7 | SF05 REGISTER x (1 is last) | 16#1D35 = 7477 | 16#202C/4E | 16#86/01/4E = 134/01/78 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF05 Reg n-7] (SRF7) | [None] (DP7)
SRF8 | SF05 REGISTER x (1 is last) | 16#1D36 = 7478 | 16#202C/4F | 16#86/01/4F = 134/01/79 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF05 Reg n-8] (SRF8) | [None] (DP8)
SRG1 | SF06 REGISTER x (1 is last) | 16#1D39 = 7481 | 16#202C/52 | 16#86/01/52 = 134/01/82 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF06 Reg n-1] (SRG1) | [None] (DP1)
SRG2 | SF06 REGISTER x (1 is last) | 16#1D3A = 7482 | 16#202C/53 | 16#86/01/53 = 134/01/83 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF06 Reg n-2] (SRG2) | [None] (DP2)
SRG3 | SF06 REGISTER x (1 is last) | 16#1D3B = 7483 | 16#202C/54 | 16#86/01/54 = 134/01/84 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF06 Reg n-3] (SRG3) | [None] (DP3)
SRG4 | SF06 REGISTER x (1 is last) | 16#1D3C = 7484 | 16#202C/55 | 16#86/01/55 = 134/01/85 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF06 Reg n-4] (SRG4) | [None] (DP4)
SRG5 | SF06 REGISTER x (1 is last) | 16#1D3D = 7485 | 16#202C/56 | 16#86/01/56 = 134/01/86 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF06 Reg n-5] (SRG5) | [None] (DP5)
SRG6 | SF06 REGISTER x (1 is last) | 16#1D3E = 7486 | 16#202C/57 | 16#86/01/57 = 134/01/87 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF06 Reg n-6] (SRG6) | [None] (DP6)
SRG7 | SF06 REGISTER x (1 is last) | 16#1D3F = 7487 | 16#202C/58 | 16#86/01/58 = 134/01/88 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF06 Reg n-7] (SRG7) | [None] (DP7)
SRG8 | SF06 REGISTER x (1 is last) | 16#1D40 = 7488 | 16#202C/59 | 16#86/01/59 = 134/01/89 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF06 Reg n-8] (SRG8) | [None] (DP8)
SRH1 | SF07 REGISTER x (1 is last) | 16#1D43 = 7491 | 16#202C/5C | 16#86/01/5C = 134/01/92 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF07 Reg n-1] (SRH1) | [None] (DP1)
SRH2 | SF07 REGISTER x (1 is last) | 16#1D44 = 7492 | 16#202C/5D | 16#86/01/5D = 134/01/93 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF07 Reg n-2] (SRH2) | [None] (DP2)
SRH3 | SF07 REGISTER x (1 is last) | 16#1D45 = 7493 | 16#202C/5E | 16#86/01/5E = 134/01/94 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF07 Reg n-3] (SRH3) | [None] (DP3)
SRH4 | SF07 REGISTER x (1 is last) | 16#1D46 = 7494 | 16#202C/5F | 16#86/01/5F = 134/01/95 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF07 Reg n-4] (SRH4) | [None] (DP4)
SRH5 | SF07 REGISTER x (1 is last) | 16#1D47 = 7495 | 16#202C/60 | 16#86/01/60 = 134/01/96 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF07 Reg n-5] (SRH5) | [None] (DP5)
SRH6 | SF07 REGISTER x (1 is last) | 16#1D48 = 7496 | 16#202C/61 | 16#86/01/61 = 134/01/97 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF07 Reg n-6] (SRH6) | [None] (DP6)
SRH7 | SF07 REGISTER x (1 is last) | 16#1D49 = 7497 | 16#202C/62 | 16#86/01/62 = 134/01/98 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF07 Reg n-7] (SRH7) | [None] (DP7)
SRH8 | SF07 REGISTER x (1 is last) | 16#1D4A = 7498 | 16#202C/63 | 16#86/01/63 = 134/01/99 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF07 Reg n-8] (SRH8) | [None] (DP8)
SRI1 | SF08 REGISTER x (1 is last) | 16#1D4D = 7501 | 16#202D/2 | 16#86/01/66 = 134/01/102 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF08 Reg n-1] (SRI1) | [None] (DP1)
SRI2 | SF08 REGISTER x (1 is last) | 16#1D4E = 7502 | 16#202D/3 | 16#86/01/67 = 134/01/103 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF08 Reg n-2] (SRI2) | [None] (DP2)
SRI3 | SF08 REGISTER x (1 is last) | 16#1D4F = 7503 | 16#202D/4 | 16#86/01/68 = 134/01/104 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF08 Reg n-3] (SRI3) | [None] (DP3)
SRI4 | SF08 REGISTER x (1 is last) | 16#1D50 = 7504 | 16#202D/5 | 16#86/01/69 = 134/01/105 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF08 Reg n-4] (SRI4) | [None] (DP4)
SRI5 | SF08 REGISTER x (1 is last) | 16#1D51 = 7505 | 16#202D/6 | 16#86/01/6A = 134/01/106 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF08 Reg n-5] (SRI5) | [None] (DP5)
SRI6 | SF08 REGISTER x (1 is last) | 16#1D52 = 7506 | 16#202D/7 | 16#86/01/6B = 134/01/107 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF08 Reg n-6] (SRI6) | [None] (DP6)
SRI7 | SF08 REGISTER x (1 is last) | 16#1D53 = 7507 | 16#202D/8 | 16#86/01/6C = 134/01/108 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF08 Reg n-7] (SRI7) | [None] (DP7)
SRI8 | SF08 REGISTER x (1 is last) | 16#1D54 = 7508 | 16#202D/9 | 16#86/01/6D = 134/01/109 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF08 Reg n-8] (SRI8) | [None] (DP8)
SRJ1 | SF09 REGISTER x (1 is last) | 16#1D57 = 7511 | 16#202D/C | 16#86/01/70 = 134/01/112 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF09 Reg n-1] (SRJ1) | [None] (DP1)
SRJ2 | SF09 REGISTER x (1 is last) | 16#1D58 = 7512 | 16#202D/D | 16#86/01/71 = 134/01/113 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF09 Reg n-2] (SRJ2) | [None] (DP2)
SRJ3 | SF09 REGISTER x (1 is last) | 16#1D59 = 7513 | 16#202D/E | 16#86/01/72 = 134/01/114 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF09 Reg n-3] (SRJ3) | [None] (DP3)
SRJ4 | SF09 REGISTER x (1 is last) | 16#1D5A = 7514 | 16#202D/F | 16#86/01/73 = 134/01/115 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF09 Reg n-4] (SRJ4) | [None] (DP4)
SRJ5 | SF09 REGISTER x (1 is last) | 16#1D5B = 7515 | 16#202D/10 | 16#86/01/74 = 134/01/116 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF09 Reg n-5] (SRJ5) | [None] (DP5)
SRJ6 | SF09 REGISTER x (1 is last) | 16#1D5C = 7516 | 16#202D/11 | 16#86/01/75 = 134/01/117 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF09 Reg n-6] (SRJ6) | [None] (DP6)
SRJ7 | SF09 REGISTER x (1 is last) | 16#1D5D = 7517 | 16#202D/12 | 16#86/01/76 = 134/01/118 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF09 Reg n-7] (SRJ7) | [None] (DP7)
SRJ8 | SF09 REGISTER x (1 is last) | 16#1D5E = 7518 | 16#202D/13 | 16#86/01/77 = 134/01/119 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF09 Reg n-8] (SRJ8) | [None] (DP8)
SRK1 | SF10 REGISTER x (1 is last) | 16#1D61 = 7521 | 16#202D/16 | 16#86/01/7A = 134/01/122 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF10 Reg n-1] (SRK1) | [None] (DP1)
SRK2 | SF10 REGISTER x (1 is last) | 16#1D62 = 7522 | 16#202D/17 | 16#86/01/7B = 134/01/123 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF10 Reg n-2] (SRK2) | [None] (DP2)
SRK3 | SF10 REGISTER x (1 is last) | 16#1D63 = 7523 | 16#202D/18 | 16#86/01/7C = 134/01/124 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF10 Reg n-3] (SRK3) | [None] (DP3)
SRK4 | SF10 REGISTER x (1 is last) | 16#1D64 = 7524 | 16#202D/19 | 16#86/01/7D = 134/01/125 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF10 Reg n-4] (SRK4) | [None] (DP4)
SRK5 | SF10 REGISTER x (1 is last) | 16#1D65 = 7525 | 16#202D/1A | 16#86/01/7E = 134/01/126 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF10 Reg n-5] (SRK5) | [None] (DP5)
SRK6 | SF10 REGISTER x (1 is last) | 16#1D66 = 7526 | 16#202D/1B | 16#86/01/7F = 134/01/127 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF10 Reg n-6] (SRK6) | [None] (DP6)
SRK7 | SF10 REGISTER x (1 is last) | 16#1D67 = 7527 | 16#202D/1C | 16#86/01/80 = 134/01/128 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF10 Reg n-7] (SRK7) | [None] (DP7)
SRK8 | SF10 REGISTER x (1 is last) | 16#1D68 = 7528 | 16#202D/1D | 16#86/01/81 = 134/01/129 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF10 Reg n-8] (SRK8) | [None] (DP8)
SRL1 | SF11 REGISTER x (1 is last) | 16#1D6B = 7531 | 16#202D/20 | 16#86/01/84 = 134/01/132 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF11 Reg n-1] (SRL1) | [None] (DP1)
SRL2 | SF11 REGISTER x (1 is last) | 16#1D6C = 7532 | 16#202D/21 | 16#86/01/85 = 134/01/133 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF11 Reg n-2] (SRL2) | [None] (DP2)
SRL3 | SF11 REGISTER x (1 is last) | 16#1D6D = 7533 | 16#202D/22 | 16#86/01/86 = 134/01/134 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF11 Reg n-3] (SRL3) | [None] (DP3)
SRL4 | SF11 REGISTER x (1 is last) | 16#1D6E = 7534 | 16#202D/23 | 16#86/01/87 = 134/01/135 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF11 Reg n-4] (SRL4) | [None] (DP4)
SRL5 | SF11 REGISTER x (1 is last) | 16#1D6F = 7535 | 16#202D/24 | 16#86/01/88 = 134/01/136 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF11 Reg n-5] (SRL5) | [None] (DP5)
SRL6 | SF11 REGISTER x (1 is last) | 16#1D70 = 7536 | 16#202D/25 | 16#86/01/89 = 134/01/137 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF11 Reg n-6] (SRL6) | [None] (DP6)
SRL7 | SF11 REGISTER x (1 is last) | 16#1D71 = 7537 | 16#202D/26 | 16#86/01/8A = 134/01/138 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF11 Reg n-7] (SRL7) | [None] (DP7)
SRL8 | SF11 REGISTER x (1 is last) | 16#1D72 = 7538 | 16#202D/27 | 16#86/01/8B = 134/01/139 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF11 Reg n-8] (SRL8) | [None] (DP8)
SS1A | Safe Stop 1 Assigment | 16#3BCE = 15310 | 16#207B/B | 16#AD/01/6F = 173/01/111 | SPSL | Safety function | R/WS | WORD (Enumeration) | - | [None] NO
SS1S | Safe stop 1 status | 16#3BD3 = 15315 | 16#207B/10 | 16#AD/01/74 = 173/01/116 | SS1S | Safety function | R | WORD (Enumeration) | - |  |  | [SS1 status] (SS1S) | [MONIT. SAFETY] (SAF)
SSRT | SS1 Ramp Value | 16#3BCF = 15311 | 16#207B/C | 16#AD/01/70 = 173/01/112 |  | Safety function | R/WS | UINT (Unsigned16) | 0.1 | 0.1 | 0.1 ... 599.0
SSRU | SS1 Ramp unit | 16#3BD0 = 15312 | 16#207B/D | 16#AD/01/71 = 173/01/113 | SSRU | Safety function | R/WS | WORD (Enumeration) | - | [None] 1H
SSSL | SS1&SLS Standstill Level | 16#3BD1 = 15313 | 16#207B/E | 16#AD/01/72 = 173/01/114 |  | Safety function | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz
SSTT | SS1 Trip Threshold | 16#3BD2 = 15314 | 16#207B/F | 16#AD/01/73 = 173/01/115 |  | Safety function | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz
STFR | Estimated stator frequency (signed value) | 16#0CD1 = 3281 | 16#2002/52 | 16#71/01/52 = 113/01/82 |  | Configuration and settings | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Stator frequency] (STFR) | [MONITORING] (MON)
STOA | STO Assignement | 16#3BD8 = 15320 | 16#207B/15 | 16#AD/01/79 = 173/01/121 | SPSL | Safety function | R/WS | WORD (Enumeration) | - | [None] NO
TAC | IGBT alarm counter | 16#0CA3 = 3235 | 16#2002/24 | 16#71/01/24 = 113/01/36 |  | Measurement parameters | R | UINT (Unsigned16) | 1 s |  | 0 s ... 65535 s | [IGBT alarm counter] (TAC) | [DIAGNOSTICS] (DGT)
TAC2 | Min IGBT frequency time | 16#0CAA = 3242 | 16#2002/2B | 16#71/01/2B = 113/01/43 |  | Measurement parameters | R | UINT (Unsigned16) | 1 s |  | 0 s ... 65535 s | [Min. freq time] (TAC2) | [DIAGNOSTICS] (DGT)
TANF | Detection time of ANF detected fault | 16#1609 = 5641 | 16#201A/2A | 16#7D/01/2A = 125/01/42 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.10 s | 0.00 s ... 10.00 s | [ANF Time Thd.] (TANF) | [ENCODER CONFIGURATION] (IEN) [ENCODER FAULT] (SDD)
TBO | Time to make a reel | 16#2FB0 = 12208 | 16#205C/9 | 16#9E/01/09 = 158/01/09 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 min | 0 min | 0 min ... 9999 min | [Reel time] (TBO) | [TRAVERSE CONTROL] (TR0)
TDN | Traverse ctrl decel time | 16#2FAF = 12207 | 16#205C/8 | 16#9E/01/08 = 158/01/08 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 4.0 s | 0.1 s ... 999.9 s | [Traverse ctrl. decel] (TDN) | [TRAVERSE CONTROL] (TR0)
TRC | Yarn control input | 16#2FA9 = 12201 | 16#205C/2 | 16#9E/01/02 = 158/01/02 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Yarn control] (TRC) | [TRAVERSE CONTROL] (TR0)
TRH | Traverse frequency high | 16#2FAA = 12202 | 16#205C/3 | 16#9E/01/03 = 158/01/03 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 4.0 Hz | 0.0 Hz ... 10.0 Hz | [Traverse freq. high] (TRH) | [SETTINGS] (SET) [TRAVERSE CONTROL] (TR0)
TRL | Traverse frequency low | 16#2FAB = 12203 | 16#205C/4 | 16#9E/01/04 = 158/01/04 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 4.0 Hz | 0.0 Hz ... 10.0 Hz | [Traverse Freq. Low] (TRL) | [SETTINGS] (SET) [TRAVERSE CONTROL] (TR0)
TSY | Sync. wobble output | 16#2FB6 = 12214 | 16#205C/F | 16#9E/01/0F = 158/01/15 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [Sync. wobble] (TSY) | [TRAVERSE CONTROL] (TR0)
TUP | Traverse ctrl accel time | 16#2FAE = 12206 | 16#205C/7 | 16#9E/01/07 = 158/01/07 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 4.0 s | 0.1 s ... 999.9 s | [Traverse ctrl. accel.] (TUP) | [TRAVERSE CONTROL] (TR0)
IPC1 | Ethernet : IP Card | 16#FAD4 = 64212 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 |  | 0 ... 255
IPC2 | Ethernet : IP Card | 16#FAD5 = 64213 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 |  | 0 ... 255
IPC3 | Ethernet : IP Card | 16#FAD6 = 64214 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 |  | 0 ... 255
IPC4 | Ethernet : IP Card | 16#FAD7 = 64215 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 |  | 0 ... 255
IPM1 | Ethernet : Subnetwork Mask | 16#FAD8 = 64216 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 |  | 0 ... 255
IPM2 | Ethernet : Subnetwork Mask | 16#FAD9 = 64217 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 |  | 0 ... 255
IPM3 | Ethernet : Subnetwork Mask | 16#FADA = 64218 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 |  | 0 ... 255
IPM4 | Ethernet : Subnetwork Mask | 16#FADB = 64219 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 |  | 0 ... 255
IPG1 | Ethernet : Gateway address | 16#FADC = 64220 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 |  | 0 ... 255
IPG2 | Ethernet : Gateway address | 16#FADD = 64221 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 |  | 0 ... 255
IPG3 | Ethernet : Gateway address | 16#FADE = 64222 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 |  | 0 ... 255
IPG4 | Ethernet : Gateway address | 16#FADF = 64223 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 |  | 0 ... 255
IPA1 | Ethernet IP: Current IP Card | 16#FAFC = 64252 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 |  | 0 ... 255
IPA2 | Ethernet IP: Current IP Card | 16#FAFD = 64253 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 |  | 0 ... 255
IPA3 | Ethernet IP: Current IP Card | 16#FAFE = 64254 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 |  | 0 ... 255
IPA4 | Ethernet IP: Current IP Card | 16#FAFF = 64255 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 |  | 0 ... 255
IPS1 | Ethernet IP: Current IP Mask | 16#FB00 = 64256 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 |  | 0 ... 255
IPS2 | Ethernet IP: Current IP Mask | 16#FB01 = 64257 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 |  | 0 ... 255
IPS3 | Ethernet IP: Current IP Mask | 16#FB02 = 64258 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 |  | 0 ... 255
IPS4 | Ethernet IP: Current IP Mask | 16#FB03 = 64259 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 |  | 0 ... 255
IPT1 | Ethernet IP: Current IP Gateway | 16#FB04 = 64260 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 |  | 0 ... 255
IPT2 | Ethernet IP: Current IP Gateway | 16#FB05 = 64261 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 |  | 0 ... 255
IPT3 | Ethernet IP: Current IP Gateway | 16#FB06 = 64262 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 |  | 0 ... 255
IPT4 | Ethernet IP: Current IP Gateway | 16#FB07 = 64263 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 |  | 0 ... 255
UNT | APH, PTH, RTH and RTHI units | 16#0CA2 = 3234 | 16#2002/23 | 16#71/01/23 = 113/01/35 |  | Configuration and settings | R | WORD (BitString16) | -
NTID | Fieldbus identifier selection | 16#1A26 = 6694 | 16#2024/5F | 16#82/01/5F = 130/01/95 | NTID | Configuration and settings | R/WS | WORD (Enumeration) | - | [ATV320 identifier] ATV320 |  | [Fieldbus Identifier Sel] (NTID) | [COMMUNICATION] (COM)

## Enumerations
List ID | Value | Display | Description
ACT | 0 | [Not done] (TAB) | Default stator resistance
| 1 | [Pending] (PEND) | Test is pending
| 2 | [In Progress] (PROG) | Test in progress
| 3 | [Failed] (FAIL) | Test has failed.
| 4 | [Done] (DONE) | Measured R.stator is used
ACTION | 0 | [No action] (NO) | No action
| 1 | [Do tune] (YES) | Do tune
| 2 | [Erase tune] (CLR) | Erase tune
ADC | 0 | [No] (NO) | No DC injected current
| 1 | [Yes] (YES) | DC inj braking selected
| 2 | [Continuous] (CT) | Continuous DC inj brake
AIOL | 0 | [0 - 100%] (POS) | Positive only
| 1 | [+/- 100%] (POSNEG) | Positive and negative
AIOT | 1 | [Voltage] (10U) | AI in voltage selected
| 2 | [Current] (0A) | AI in current selected
| 5 | [Voltage +/-] (N10U) | AI bipolar volts selected
AST | 3 | [IPM align.] (IPMA) | IPM alignment
| 4 | [SPM align] (SPMA) | SPM alignment
| 5 | [PSI align.] (PSI) | Pulse Signal Injection
| 6 | [PSIO align.] (PSIO) | Pulse Signal Injection - Optimized
| 254 | [No align.] (NO) | NO alignment
AUT | 0 | [No] (NO) | No
| 1 | [Yes] (YES) | At each power on
| 2 | [One] (ONE) | At first run order
BDCO | 38 | [50 kbps] (50K) | Baud rate 50kbps
| 52 | [125 kbps] (125K) | Baud rate 125kbps
| 60 | [250 kbps] (250K) | Baud rate 250kbps
| 68 | [500 kbps] (500K) | Baud rate 500kbps
| 76 | [1 Mbps] (1M) | Baud rate 1Mbps
BFR | 0 | [50Hz IEC] (50Hz) | 50Hz Motor frequency
| 1 | [60Hz NEMA] (60Hz) | 60Hz Motor frequency
BIP | 0 | [No] (NO) | No
| 1 | [Yes] (YES) | Brake impulse Fwd
| 2 | [2 IBR] (2IBR) | Brake impulse Fwd/Rev
BLC | 0 | [No] (NO) | No
| 2 | [R2] (R2) | Relay R2
| 17 | [LO1] (LO1) | Logic output 1
| 64 | [DO1] (DO1) | Logic output on AO1
BMP | 0 | [Stop] (STOP) | Cmd/ref clear on c/over
| 1 | [Bumpless] (BUMP) | Cmd/ref copied on c/over
BOA | 0 | [Inactive] (NO) | Inactive
| 1 | [Dynamic] (DYNA) | Dynamic
| 2 | [Static] (STAT) | Static
BRA | 0 | [No] (NO) | Braking cmd transistor
| 1 | [Yes] (YES) | Dec ramp adapt assigned
| 2 | [High torq. A] (DYNA) | Dynamic high torque A
BSP | 0 | [Standard] (BSD) | Standard ref template
| 1 | [Pedestal] (BLS) | Pedestal at LSP
| 2 | [Deadband] (BNS) | Deadband at LSP
| 4 | [Deadband 0] (BNS0) | Deadband at 0 speed
BST | 0 | [Traveling] (HOR) | Cross traverse motion
| 1 | [Hoisting] (VER) | Hoisting motion
CDX | 1 | [Terminals] (TER) | Terminal block
| 2 | [Local] (LOC) | Local control
| 3 | [HMI] (LCC) | Local HMI
| 10 | [Modbus] (MDB) | Modbus communication
| 20 | [CANopen] (CAN) | CANopen communication
| 30 | [Com. card] (NET) | Ext. communication card
CFG | 0 | [Start/Stop] (STS) | Standard Start/Stop
| 1 | [M. handling] (HDG) | Material handling
| 2 | [Hoisting] (HST) | Hoisting
| 3 | [Gen. Use] (GEN) | General use
| 4 | [PID regul.] (PID) | PID regulation
| 5 | [Network C.] (NET) | Network communications
CFPS | 0 | [None] (NO) | Not Assigned
| 1 | [Set n°1] (CFP1) | Parameter set 1
| 2 | [Set n°2] (CFP2) | Parameter set 2
| 3 | [Set n°3] (CFP3) | Parameter set 3
CHCF | 1 | [Not separ.] (SIM) | Combined channel mode
| 2 | [Separate] (SEP) | Separated channel mode
| 3 | [I/O profile] (IO) | I/O mode
CIOA | 0 | [20/70] (20) | 20/70
| 1 | [21/71] (21) | 21/71
| 2 | [100/101] (100) | 100/101
| 3 | [Unconfig.] (UNCG) | Unconfigured
CNFS | 0 | [In progress] (NO) | Not assigned
| 1 | [Config. n°0] (CNF0) | Configuration set 1
| 2 | [Config. n°1] (CNF1) | Configuration set 2
| 3 | [Config. n°2] (CNF2) | Configuration set 3
CNL | 0 | [Terminals] (TER) | Terminal block
| 1 | [Local] (LOC) | Local
| 2 | [HMI] (LCC) | Local HMI
| 3 | [Modbus] (MDB) | Modbus communication 1
| 6 | [CANopen] (CAN) | CANopen communication
| 7 | [+/- speed] (TUD) | Increase/Decrease speed
| 8 | [LUD->NotDef] (LUD) | LUD->NotDef
| 9 | [Com. card] (NET) | Ext. communication card
| 14 | [Mfg] (IND) | Indus
| 15 | [PC tool] (PWS) | PC tool
COP | 0 | [No] (NO) | No copy
| 1 | [Reference] (SP) | Copy reference
| 2 | [Command] (CD) | Copy control
| 3 | [Cmd + ref.] (ALL) | Copy control & reference
CSLFN | 0 | [No] (NO) | Not assigned
| 180 | [Jog] (FNJOG) | Jog
| 181 | [Preset spd2] (FNPS1) | Speed reference 1
| 182 | [Preset spd3] (FNPS2) | Speed reference 2
| 183 | [PID ref. 2] (FNPR1) | PID reference 1
| 184 | [PID ref. 3] (FNPR2) | PID reference 2
| 185 | [+Speed] (FNUSP) | Increase speed
| 186 | [-Speed] (FNDSP) | Decrease speed
| 187 | [T/K] (FNTK) | Terminal keypad
CSLOUT | 0 | [No] (NO) | Not assigned
| 146 | [R2] (R2) | Relay R2
| 129 | [LO1] (LO1) | Logical output LO1
| 161 | [DO1] (DO1) | Logic output on AO1
CTT | 0 | [SVC V] (VVC) | Sensorless flux vector V
| 3 | [Standard] (STD) | Standard motor law
| 4 | [V/F 5pts] (UF5) | 5 point voltage/frequency
| 5 | [Sync. mot.] (SYN) | Synchronous motor
| 6 | [V/F Quad.] (UFQ) | V/F Quadratic
| 7 | [Energy Sav.] (NLD) | Energy Saving
DANF | 0 | [Over] (OVER) | Trip in case of overspeed
| 1 | [Both] (BOTH) | Trip in case of overspeed or underspeed
DCCC | 0 | [Altivar] (ATV) | Altivar compatibility
| 1 | [Lexium] (LHM) | Lexium compatibility
DCCM | 0 | [No] (NO) | No
| 1 | [Bus & Main] (MAIN) | Bus and Main
| 2 | [Only Bus] (BUS) | Only Bus
DOTD | 0 | [Freewheel] (NST) | Drive freewheel stopping
| 1 | [Ramp stop] (RMP) | Ramp stop on fault
DPMA | 1 | [MCL1] (1) | MCL1
| 2 | [MCL2] (2) | MCL2
DSF | 0 | [Standard] (STD) | Standard
| 1 | [Optimized] (OPT) | Optimized
DUR | 0 | [5 minutes] (5) | 5 minutes
| 1 | [10 minutes] (10) | 10 minutes
| 2 | [30 minutes] (30) | 30 minutes
| 3 | [1 hour] (1H) | 1 hour
| 4 | [2 hours] (2H) | 2 hours
| 5 | [3 hours] (3H) | 3 hours
| 6 | [Unlimited] (CT) | Unlimited
EBHT | 0 | [No] (NO) | Not configured
| 1 | [RS422 5V] (RS05) | RS422 5V
| 2 | [Push Pull 24V] (PP24) | Push Pull 24V
| 3 | [Open collector 15V] (OC15) | Open collector 15V
| 4 | [Open collector 12V] (OC12) | Open collector 12V
| 5 | [RS422 15V] (RS15) | RS422 15V
| 6 | [Push Pull 15V] (PP15) | Push Pull 15V
| 7 | [Push Pull 12V] (PP12) | Push Pull 12V
ECFG | 0 | [Ignore] (NO) | Ignore phase loss
| 1 | [Freewheel] (YES) | Freewheel stop on fault
| 2 | [Per STT] (STT) | Per STT
| 4 | [fallback spd] (LFF) | Fallback speed on fault
| 5 | [Spd maint.] (RLS) | Maintain speed at fault
| 6 | [Ramp stop] (RMP) | Ramp stop on fault
| 7 | [Fast stop] (FST) | Fast stop on fault
| 8 | [DC injection] (DCI) | DC injection on fault
ENS | 1 | [AABB] (AABB) | For signals A/A-/B/B-
| 2 | [AB] (AB) | For signals A/B
ENU | 0 | [No] (NO) | Inactive
| 1 | [Fdbk monit.] (SEC) | Speed feedback monitor
ERRD | 16#0000 | [No fault] (NOF) | No fault saved
| 16#1000 | [Precharge] (CRF1) | Precharge
| 16#1000 | [Motor overload] (OLF) | Motor overload fault
| 16#1000 | [Overspeed] (SOF) | Motor overspeed fault
| 16#1000 | [IGBT desaturation] (HDF) | IGBT desaturation
| 16#1000 | [internal- CPU ] (INFE) | internal- CPU
| 16#1000 | [Ch.sw. fault] (CSF) | Channel switching fault
| 16#1000 | [Angle error] (ASF) | Angle error
| 16#2230 | [IGBT short circuit] (SCF4) | IGBT short circuit fault
| 16#2310 | [Overcurrent] (OCF) | Overcurrent fault
| 16#2311 | [Proc.Overload Flt] (OLC) | Process Overload Fault
| 16#2320 | [Motor short circuit] (SCF1) | Motor short circuit
| 16#2320 | [Motor short circuit] (SCF5) | motor short circuit
| 16#2330 | [Ground short circuit] (SCF3) | Ground short circuit
| 16#3110 | [Mains overvoltage] (OSF) | Supply overvoltage fault
| 16#3120 | [Undervoltage] (USF) | Supply undervolt fault
| 16#3130 | [Input phase loss] (PHF) | Supply phase loss fault
| 16#3310 | [Overbraking] (OBF) | DC bus overvoltage fault
| 16#3310 | [1 output phase loss] (OPF1) | 1 motor phase loss fault
| 16#3310 | [3out ph loss] (OPF2) | 3 motor phase loss fault
| 16#4210 | [Drive overheat] (OHF) | Drive overheating fault
| 16#4210 | [IGBT overheat] (TJF) | IGBT overheat fault
| 16#4310 | [PTC fault] (OTFL) | LI6=PTC overheat fault
| 16#5000 | [Out. contact. stuck] (FCF1) | Output cont close fault
| 16#5000 | [Out. contact. open.] (FCF2) | Output cont open fault
| 16#5000 | [input contactor] (LCF) | input contactor
| 16#5210 | [Internal- I measure] (INF9) | Internal I measure fault
| 16#5210 | [Internal-mains circuit] (INFA) | Internal i/p volt circuit flt
| 16#5210 | [Internal- th. sensor] (INFB) | Internal temperature fault
| 16#5530 | [Control Eeprom] (EEF1) | EEprom control fault
| 16#5530 | [Power Eeprom] (EEF2) | EEprom power fault
| 16#6100 | [Rating error] (INF1) | Rating error
| 16#6100 | [PWR Calib.] (INF2) | Incompatible control card
| 16#6100 | [Int.serial link] (INF3) | Internal coms link fault
| 16#6100 | [Int.Mfg area] (INF4) | Internal manu zone fault
| 16#6100 | [Cards pairing] (HCF) | Cards pairing
| 16#6300 | [Incorrect config.] (CFF) | Incorrect configuration
| 16#6300 | [Invalid config.] (CFI) | Invalid config parameters
| 16#6300 | [Bad conf] (CFI2) | Interrupted config.
| 16#7000 | [Internal-option] (INF6) | Internal option fault
| 16#7110 | [Brake feedback] (BRF) | Brake feedback fault
| 16#7300 | [Load slipping] (ANF) | Output speed <> ref
| 16#7300 | [LI6=PTC probe] (PTFL) | LI6=PTC failed
| 16#7300 | [AI3 4-20mA loss] (LFF3) | AI3 4-20mA loss
| 16#7310 | [Speed fdback loss] (SPF) | Speed feedback loss
| 16#7400 | [FB fault] (FBE) | FB fault
| 16#7400 | [FB stop flt.] (FBES) | FB stop fault
| 16#7510 | [Modbus com.] (SLF1) | Modbus coms fault
| 16#7510 | [HMI com.] (SLF3) | HMI coms fault
| 16#7520 | [int. com.link] (ILF) | Com Internal link fault
| 16#7520 | [Com. network] (CNF) | Network fault
| 16#7530 | [PC com.] (SLF2) | PC coms fault
| 16#8100 | [CAN com.] (COF) | Comms fault CANopen
| 16#9000 | [External flt-LI/Bit] (EPF1) | External fault logic input
| 16#9000 | [External fault com.] (EPF2) | External fault comms
| 16#FF00 | [Auto-tuning ] (TNF) | Auto-tuning fault
| 16#FF01 | [Brake control] (BLF) | Brake control fault
| 16#FF02 | [Torque/current lim] (SSF) | Torque/current limit fault
| 16#FF03 | [Pr.Underload.Flt] (ULF) | Process Underlaod Fault
| 16#FF03 | [Safety fault] (SAFF) | Safety fault
| 16#FF80 | [Load fault] (DLF) | Dynamic load fault
ETHM | 0 | [ModbusTCP] (MBTP) | ModbusTCP
| 1 | [EthernetIP] (ETIP) | EthernetIP
ETST | 1 | [Init] (INIT) | Init
| 2 | [PreOp] (PROP) | PreOp
| 3 | [Boot] (BOOT) | Boot
| 4 | [SafeOp] (SFOP) | SafeOp
| 8 | [Op] (OP) | Op
FBFT | 0 | [No] (NO) | No
| 1 | [Internal] (INT) | Internal
| 2 | [Binary file] (BIN) | Binary file
| 3 | [Intern para.] (INP) | Internal parameters
| 4 | [Para. RW] (PAR) | Parameter access on read or write
| 5 | [Calculation] (CAL) | Calculation
| 6 | [TO AUX] (TOAU) | TimeOut AUX task
| 7 | [TO synch] (TOPP) | TimeOut in synchronous tasks
| 8 | [Bad ADLC] (ADL) | ADLC with bad parameter
| 9 | [Input assig.] (IN) | Inputs assignment
FBST | 0 | [Idle] (IDLE) | Idle
| 1 | [Check prog.] (CHEC) | Check program
| 2 | [Stop] (STOP) | Stop
| 3 | [Init] (INIT) | Init
| 4 | [Run] (RUN) | Run
| 5 | [Error] (ERR) | Error
FCS | 0 | [NO] (NO) | No
| 2 | [Internal 1] (REC1) | Restore internal conf. 1
| 3 | [None] (REC2)
| 64 | [Factory set.] (INI) | Factory settings
| 71 | [None] (INI1)
FFM | 0 | [Standard] (STD) | Standard
| 1 | [Always] (RUN) | Always
| 2 | [Never] (STP) | Never
FLU | 0 | [Not cont.] (FNC) | Flux on run signal
| 1 | [Continuous] (FCT) | Pre flux on power up
| 2 | [No] (FNO) | No Pre fluxing
FOR | 0 | [No] (NO) | Not configured
| 1 | [AUTO] (AUTO) | Automatic format
| 2 | [8-O-1] (8O1) | 8bit odd parity 1stop bit
| 3 | [8-E-1] (8E1) | 8bit even parity 1stop bit
| 4 | [8-N-1] (8N1) | 8bit no parity 1stop bit
| 5 | [8-N-2] (8N2) | 8bit no parity 2stop bits
| 6 | [7-O-1] (7O1) | 7bit odd parity 1stop bit
| 7 | [7-E-1] (7E1) | 7bit even parity 1stop bit
| 8 | [7-O-2] (7O2) | 7bit odd parity 2stop bits
| 9 | [7-E-2] (7E2) | 7bit even parity 2stop bits
GDLS | 0 | [None] (NO)
| 1 | [None] (OFF)
| 2 | [None] (STD)
| 3 | [None] (LGD)
| 4 | [None] (ON)
| 5 | [None] (FLT)
HMIS | 0 | [Auto-tuning] (TUN) | Drive automatic tuning
| 1 | [In DC inject.] (DCB) | Drive DC inj braking
| 2 | [Ready] (RDY) | Drive ready
| 3 | [Freewheel] (NST) | Drive freewheel stopping
| 4 | [Drv running] (RUN) | Drive running
| 5 | [In accel.] (ACC) | Drive accelerating
| 6 | [In decel.] (DEC) | Drive decelerating
| 7 | [Current lim.] (CLI) | Drive in current limit
| 8 | [Fast stop] (FST) | Drive fast stopping
| 9 | [Mot. fluxing] (FLU) | Drive fluxing motor
| 11 | [no mains V.] (NLP) | Drive no line voltage
| 12 | [Active PWR] (PRA) | Drive in power removal
| 13 | [control.stop] (CTL) | Drive control stopping
| 14 | [Dec. adapt.] (OBR) | Drive dec ramp adaption
| 15 | [Output cut] (SOC) | Drive cutting output
| 17 | [UnderV. al.] (USA) | Drive undervoltage alarm
| 18 | [In mfg. test] (TC) | Drive test in progress
| 19 | [in autotest] (ST) | In autotest
| 20 | [autotest err] (FA) | Autotest err
| 21 | [Autotest OK] (OK) | Autotest OK
| 22 | [eeprom test] (EP) | Eeprom test
| 23 | [In fault] (FLT) | Product in fault
| 25 | [DCP] (DCP) | DCP
| 28 | [SS1 active] (SS1) | SS1 active
| 29 | [SLS active] (SLS) | SLS active
| 30 | [STO active] (STO) | STO active
| 31 | [None] (SMS)
| 32 | [None] (GDL)
HSO | 0 | [No] (NO) | Inactive
| 1 | [Speed ref] (SSO) | Speed reference mode
| 2 | [I Limit] (CSO) | Current limit mode
INCPER | 0 | [0,01%] (001) | 0,01%
| 1 | [0,1%] (01) | 0,1%
| 2 | [1%] (1) | 1%
INR | 0 | [0.01] (001) | hundreds of seconds
| 1 | [0.1] (01) | tenths of seconds
| 2 | [1] (1) | seconds
IPAE | 0 | [Idle state] (IDLE) | idle state
| 1 | [Initialization] (INIT) | initialization
| 2 | [Config] (CONF) | configuration
| 3 | [Ready] (RDY) | ready
| 4 | [Operation.] (OPE) | operationnal
| 5 | [Unconfig.] (UCFG) | not configured
| 6 | [Unrec. fault] (UREC) | Unrecoverable fault
IPM | 0 | [Fixed] (MANU) | Fixed address
| 1 | [BOOTP] (BOOTP) | BOOTP
| 2 | [DHCP] (DHCP) | DHCP
| 3 | [DCP] (DCP) | DCP
LFT | 0 | [No fault] (NOF) | No fault saved
| 2 | [Control Eeprom] (EEF1) | EEprom control fault
| 3 | [Incorrect config.] (CFF) | Incorrect configuration
| 4 | [Invalid config.] (CFI) | Invalid config parameters
| 5 | [Modbus com.] (SLF1) | Modbus coms fault
| 6 | [int. com.link] (ILF) | Com Internal link fault
| 7 | [Com. network] (CNF) | Network fault
| 8 | [External flt-LI/Bit] (EPF1) | External fault logic input
| 9 | [Overcurrent] (OCF) | Overcurrent fault
| 10 | [Precharge] (CRF1) | Precharge
| 11 | [Speed fdback loss] (SPF) | Speed feedback loss
| 12 | [Load slipping] (ANF) | Output speed <> ref
| 16 | [Drive overheat] (OHF) | Drive overheating fault
| 17 | [Motor overload] (OLF) | Motor overload fault
| 18 | [Overbraking] (OBF) | DC bus overvoltage fault
| 19 | [Mains overvoltage] (OSF) | Supply overvoltage fault
| 20 | [1 output phase loss] (OPF1) | 1 motor phase loss fault
| 21 | [Input phase loss] (PHF) | Supply phase loss fault
| 22 | [Undervoltage] (USF) | Supply undervolt fault
| 23 | [Motor short circuit] (SCF1) | Motor short circuit
| 24 | [Overspeed] (SOF) | Motor overspeed fault
| 25 | [Auto-tuning ] (TNF) | Auto-tuning fault
| 26 | [Rating error] (INF1) | Rating error
| 27 | [PWR Calib.] (INF2) | Incompatible control card
| 28 | [Int.serial link] (INF3) | Internal coms link fault
| 29 | [Int.Mfg area] (INF4) | Internal manu zone fault
| 30 | [Power Eeprom] (EEF2) | EEprom power fault
| 32 | [Ground short circuit] (SCF3) | Ground short circuit
| 33 | [3out ph loss] (OPF2) | 3 motor phase loss fault
| 34 | [CAN com.] (COF) | Comms fault CANopen
| 35 | [Brake control] (BLF) | Brake control fault
| 38 | [External fault com.] (EPF2) | External fault comms
| 41 | [Brake feedback] (BRF) | Brake feedback fault
| 42 | [PC com.] (SLF2) | PC coms fault
| 44 | [Torque/current lim] (SSF) | Torque/current limit fault
| 45 | [HMI com.] (SLF3) | HMI coms fault
| 49 | [LI6=PTC probe] (PTFL) | LI6=PTC failed
| 50 | [PTC fault] (OTFL) | LI6=PTC overheat fault
| 51 | [Internal- I measure] (INF9) | Internal I measure fault
| 52 | [Internal-mains circuit] (INFA) | Internal i/p volt circuit flt
| 53 | [Internal- th. sensor] (INFB) | Internal temperature fault
| 54 | [IGBT overheat] (TJF) | IGBT overheat fault
| 55 | [IGBT short circuit] (SCF4) | IGBT short circuit fault
| 56 | [Motor short circuit] (SCF5) | motor short circuit
| 58 | [Out. contact. stuck] (FCF1) | Output cont close fault
| 59 | [Out. contact. open.] (FCF2) | Output cont open fault
| 64 | [input contactor] (LCF) | input contactor
| 67 | [IGBT desaturation] (HDF) | IGBT desaturation
| 68 | [Internal-option] (INF6) | Internal option fault
| 69 | [internal- CPU ] (INFE) | internal- CPU
| 71 | [AI3 4-20mA loss] (LFF3) | AI3 4-20mA loss
| 73 | [Cards pairing] (HCF) | Cards pairing
| 76 | [Load fault] (DLF) | Dynamic load fault
| 77 | [Bad conf] (CFI2) | Interrupted config.
| 99 | [Ch.sw. fault] (CSF) | Channel switching fault
| 100 | [Pr.Underload.Flt] (ULF) | Process Underlaod Fault
| 101 | [Proc.Overload Flt] (OLC) | Process Overload Fault
| 105 | [Angle error] (ASF) | Angle error
| 107 | [Safety fault] (SAFF) | Safety fault
| 108 | [FB fault] (FBE) | FB fault
| 109 | [FB stop flt.] (FBES) | FB stop fault
L_H | 0 | [Active low] (LO) | Active low
| 1 | [Active high] (HIG) | Active high
MPC | 0 | [Mot Power] (NPR) | Nominal motor Power
| 1 | [Mot Cos] (COS) | Nominal motor cos Phi
NCV | 0 | [Unknown rating] (NO) | Unknown rating
| 1 | [0,12kW] (U010) | 0.10kW - 0.2HP
| 2 | [0,18kW / 0.25HP] (U018) | 0.18kW - 0.25HP
| 3 | [0,25kW] (U025) | 0.25kW - 0.37HP
| 4 | [0,37kW / 0.5HP] (U037) | 0.37kW - 0.5HP
| 5 | [0,55kW / 0.75HP] (U055) | 0.55kW - 0.75HP
| 6 | [0,75kW / 1HP] (U075) | 0.75kW - 1HP
| 7 | [5,5kW / 7.5HP] (U090) | 5.5kW - 7.5HP
| 8 | [1,1kW / 1.5HP] (U110) | 1.1kW - 1.5HP
| 9 | [1,5kW / 2HP] (U150) | 1.5kW - 2HP
| 10 | [1,85kW] (U185) | 1.85kW - 3HP
| 11 | [2,2kW / 3HP] (U220) | 2.2kW - 3HP
| 12 | [3kW] (U300) | 3kW - 4HP
| 13 | [4kW / 5HP] (U370) | 3.7kW - 5HP
| 14 | [4kW / 5HP] (U400) | 4kW - 5HP
| 15 | [5,5kW / 7.5HP] (U550) | 5.5kW - 7.5HP
| 16 | [7,5kW / 10HP] (U750) | 7.5kW - 10HP
| 17 | [9kW] (U900) | 9kW - 11HP
| 18 | [11kW / 15HP] (D110) | 11kW - 15 Hp
| 19 | [15kW / 20HP] (D150) | 15kW - 20 HP
| 20 | [18,5kW / 25HP] (D185) | 18.5kW - 25HP
| 21 | [22kW / 30HP] (D220) | 22kW - 30HP
| 22 | [30kW / 40HP] (D300) | 30kW - 40HP
NPL | 0 | [1] (POS) | 1
| 1 | [0] (NEG) | 0
NTID | 0 | [ATV320] (ATV320) | ATV320 identifier
| 1 | [ATV32] (ATV32) | ATV32 identifier
N_Y | 0 | [No] (NO) | No
| 1 | [Yes] (YES) | Yes
ONOFF | 0 | [OFF] (OFF) | OFF
| 1 | [ON] (ON) | ON
OPL | 0 | [No] (NO) | Inactive
| 1 | [Yes] (YES) | OPF fault
| 2 | [Output cut] (OAC) | No fault triggered
PRFL | 0 | [Unconfig.] (UNCG) | Unconfigured
| 1 | [1] (1) | 1
| 2 | [2] (2) | 2
| 7 | [7] (7) | 7
| 9 | [9] (9) | 9
| 100 | [100] (100) | 100
| 101 | [101] (101) | 101
| 102 | [102] (102) | 102
PSA | 0 | [No] (NO) | Not assigned
| 1 | [AI1] (AI1) | Analog input AI1
| 2 | [AI2] (AI2) | Analog input AI2
| 3 | [AI3] (AI3) | Analog input AI3
| 129 | [I motor] (OCR) | Motor current
| 130 | [Motor freq.] (OFR) | Motor frequency
| 131 | [Ramp out.] (ORP) | Ramp output
| 132 | [Motor torq.] (TRQ) | Motor torque
| 133 | [Sign. torque] (STQ) | Signed torque
| 134 | [sign ramp] (ORS) | Signed ramp
| 135 | [PID ref.] (OPS) | PID reference
| 136 | [PID feedbk] (OPF) | PID feedback
| 137 | [PID error] (OPE) | PID error
| 138 | [PID output] (OPI) | PID output
| 139 | [Mot. power] (OPR) | Drive output power
| 140 | [Mot thermal] (THR) | Motor thermal state
| 141 | [Drv thermal] (THD) | Drive thermal state
| 142 | [Torque 4Q] (TQMS) | Master / Slave torque
| 160 | [+/-Speed] (UPDT) | INC/DEC speed via LI
| 161 | [+/-spd HMI] (UPDH) | INC/DEC speed via HMI
| 163 | [HMI] (LCC) | Ref. via remote terminal
| 164 | [Modbus] (MDB) | Reference via Modbus
| 167 | [CANopen] (CAN) | Reference via CANopen
| 169 | [Com. card] (NET) | Reference via Com card
| 173 | [Sig. o/p frq.] (OFS) | Signed output frequency
| 174 | [Mot therm2] (THR2) | Motor thermal 2 state
| 175 | [Mot therm3] (THR3) | Motor thermal 3 state
| 179 | [Torque lim.] (TQL) | Torque limit
| 180 | [Motor volt.] (UOP) | Motor voltage
| 181 | [RP] (PI) | Pulse input
| 183 | [AI Virtual 1] (AIV1) | AI Virtual 1
| 184 | [DO1] (DO1) | Logic output on AO1
| 185 | [AI Virtual 2] (AIV2) | AI Virtual 2
| 240 | [OA01] (OA01) | OA01
| 241 | [OA02] (OA02) | OA02
| 242 | [OA03] (OA03) | OA03
| 243 | [OA04] (OA04) | OA04
| 244 | [OA05] (OA05) | OA05
| 245 | [OA06] (OA06) | OA06
| 246 | [OA07] (OA07) | OA07
| 247 | [OA08] (OA08) | OA08
| 248 | [OA09] (OA09) | OA09
| 249 | [OA10] (OA10) | OA10
PSL | 0 | [No] (NO) | Not assigned
| 1 | [No drive flt] (FLT) | No drive flt
| 2 | [Drv running] (RUN) | Drive running
| 3 | [Output cont] (OCC) | Ouput contactor control
| 4 | [Freq.Th.att.] (FTA) | Freq. threshold reached
| 5 | [HSP attain.] (FLA) | High speed reached
| 6 | [I attained] (CTA) | I threshold reached
| 7 | [Freq.ref.att] (SRA) | Freq. reference reached
| 8 | [Th.mot. att.] (TSA) | Mot. therm thres reach
| 9 | [Brk control] (BLC) | Brake control command
| 10 | [PID error al.] (PEE) | PID error alarm
| 11 | [PID fdbk al.] (PFA) | PID feedback alarm
| 13 | [FreqTh.att.2] (F2A) | FreqTh.att.2
| 14 | [Th. drv. att.] (TAD) | Drive thermal attained
| 21 | [Pro.Undload] (ULA) | Process underload alarm
| 22 | [Ovld.P.Alrm] (OLA) | Overload Process Alarm
| 27 | [Rope slack] (RSDA) | Rope slack alarm
| 28 | [High tq. att.] (TTHA) | High torque alarm
| 29 | [Low tq. att.] (TTLA) | Low torque alarm
| 30 | [Forward] (MFRD) | Run forward
| 31 | [Reverse] (MRRS) | Run reverse
| 37 | [Th.mot2 att] (TS2) | Mot. therm thres 2 reach
| 38 | [Th.mot3 att] (TS3) | Mot. therm thres 3 reach
| 47 | [Neg Torque] (ATS) | Negative torque
| 48 | [Cnfg.0 act.] (CNF0) | Configuration 0 active
| 49 | [Cnfg.1 act.] (CNF1) | Configuration 1 active
| 50 | [Cnfg.2 act.] (CNF2) | Configuration 2 active
| 52 | [set 1 active] (CFP1) | Parameter set 1 active
| 53 | [set 2 active] (CFP2) | Parameter set 2 active
| 54 | [set 3 active] (CFP3) | Parameter set 3 active
| 64 | [DC charged] (DBL) | DC bus charged
| 65 | [In braking] (BRS) | In braking sequence
| 66 | [P. removed] (PRM) | Power Removal state
| 72 | [Fr.met. alar.] (FQLA) | Frequency meter Alarm
| 73 | [Input cont.] (LLC) | Line contactor control
| 77 | [I present] (MCP) | I present
| 78 | [Limit sw.att] (LSA) | FDC limit attained
| 79 | [Load alarm] (DLDA) | Dynamic load alarm
| 80 | [Alarm Grp 1] (AG1) | Alarm group 1
| 81 | [Alarm Grp 2] (AG2) | Alarm group 2
| 82 | [Alarm Grp 3] (AG3) | Alarm group 3
| 85 | [LI6=PTC al.] (PLA) | LI6=PTC al.
| 87 | [Ext. fault al] (EFA) | External fault alarm
| 88 | [Under V. al.] (USA) | Under voltage alarm
| 89 | [Uvolt warn] (UPA) | Under volt warn alarm
| 91 | [Al. °C drv.] (THA) | Drive thermal alarm
| 95 | [Lim T/I att.] (SSA) | Limit torque / I attained
| 96 | [ch1 active] (FR1) | Command ch = ch 1
| 97 | [ch2 active] (FR2) | Command ch = ch 1B
| 98 | [ch1 active] (CD1) | Control ch. = Channel 1
| 99 | [ch2 active] (CD2) | Control ch. = Channel 2
| 100 | [ch1B active] (FR1B) | Command ch = ch 1B
| 101 | [Spool end] (EBO) | Spool end
| 102 | [Sync wobbl] (TSY) | Sync wobbl
| 104 | [IGBT al.] (TJA) | IGBT transistor alarm
| 107 | [AI3 Al. 4-20] (AP3) | 4-20 loss AI3
| 116 | [SHORT#FN1] (FN1) | Function key 1
| 117 | [SHORT#FN2] (FN2) | Function key 2
| 118 | [SHORT#FN3] (FN3) | Function key 3
| 119 | [SHORT#FN4] (FN4) | Function key 4
| 127 | [Ready] (RDY) | Ready
| 128 | [Yes] (YES) | Yes
| 129 | [LI1] (LI1) | Logic input LI1
| 130 | [LI2] (LI2) | Logic input LI2
| 131 | [LI3] (LI3) | Logic input LI3
| 132 | [LI4] (LI4) | Logic input LI4
| 133 | [LI5] (LI5) | Logic input LI5
| 134 | [LI6] (LI6) | Logic input LI6
| 143 | [LAI1] (LAI1) | Logic input AI1
| 144 | [LAI2] (LAI2) | Logic input AI2
| 158 | [None] (TDC)
| 160 | [CD00] (CD00) | Bit 0 logic input ctrl word
| 161 | [CD01] (CD01) | Bit 1 logic input ctrl word
| 162 | [CD02] (CD02) | Bit 2 logic input ctrl word
| 163 | [CD03] (CD03) | Bit 3 logic input ctrl word
| 164 | [CD04] (CD04) | Bit 4 logic input ctrl word
| 165 | [CD05] (CD05) | Bit 5 logic input ctrl word
| 166 | [CD06] (CD06) | Bit 6 logic input ctrl word
| 167 | [CD07] (CD07) | Bit 7 logic input ctrl word
| 168 | [CD08] (CD08) | Bit 8 logic input ctrl word
| 169 | [CD09] (CD09) | Bit 9 logic input ctrl word
| 170 | [CD10] (CD10) | Bit10 logic input ctrl word
| 171 | [CD11] (CD11) | Bit11 logic input ctrl word
| 172 | [CD12] (CD12) | Bit12 logic input ctrl word
| 173 | [CD13] (CD13) | Bit13 logic input ctrl word
| 174 | [CD14] (CD14) | Bit14 logic input ctrl word
| 175 | [CD15] (CD15) | Bit15 logic input ctrl word
| 176 | [C100] (C100) | Bit 0 Modbus ctrl word
| 177 | [C101] (C101) | Bit 1 Modbus ctrl word
| 178 | [C102] (C102) | Bit 2 Modbus ctrl word
| 179 | [C103] (C103) | Bit 3 Modbus ctrl word
| 180 | [C104] (C104) | Bit 4 Modbus ctrl word
| 181 | [C105] (C105) | Bit 5 Modbus ctrl word
| 182 | [C106] (C106) | Bit 6 Modbus ctrl word
| 183 | [C107] (C107) | Bit 7 Modbus ctrl word
| 184 | [C108] (C108) | Bit 8 Modbus ctrl word
| 185 | [C109] (C109) | Bit 9 Modbus ctrl word
| 186 | [C110] (C110) | Bit 10 Modbus ctrl word
| 187 | [C111] (C111) | Bit 11 Modbus ctrl word
| 188 | [C112] (C112) | Bit 12 Modbus ctrl word
| 189 | [C113] (C113) | Bit 13 Modbus ctrl word
| 190 | [C114] (C114) | Bit 14 Modbus ctrl word
| 191 | [C115] (C115) | Bit 15 Modbus ctrl word
| 192 | [C200] (C200) | Bit 0 CANopen ctrl word
| 193 | [C201] (C201) | Bit 1 CANopen ctrl word
| 194 | [C202] (C202) | Bit 2 CANopen ctrl word
| 195 | [C203] (C203) | Bit 3 CANopen ctrl word
| 196 | [C204] (C204) | Bit 4 CANopen ctrl word
| 197 | [C205] (C205) | Bit 5 CANopen ctrl word
| 198 | [C206] (C206) | Bit 6 CANopen ctrl word
| 199 | [C207] (C207) | Bit 7 CANopen ctrl word
| 200 | [C208] (C208) | Bit 8 CANopen ctrl word
| 201 | [C209] (C209) | Bit 9 CANopen ctrl word
| 202 | [C210] (C210) | Bit 10 CANopen ctrl word
| 203 | [C211] (C211) | Bit 11 CANopen ctrl word
| 204 | [C212] (C212) | Bit 12 CANopen ctrl word
| 205 | [C213] (C213) | Bit 13 CANopen ctrl word
| 206 | [C214] (C214) | Bit 14 CANopen ctrl word
| 207 | [C215] (C215) | Bit 15 CANopen ctrl word
| 208 | [C300] (C300) | Bit 0 Com card ctrl word
| 209 | [C301] (C301) | Bit 1 Com card ctrl word
| 210 | [C302] (C302) | Bit 2 Com card ctrl word
| 211 | [C303] (C303) | Bit 3 Com card ctrl word
| 212 | [C304] (C304) | Bit 4 Com card ctrl word
| 213 | [C305] (C305) | Bit 5 Com card ctrl word
| 214 | [C306] (C306) | Bit 6 Com card ctrl word
| 215 | [C307] (C307) | Bit 7 Com card ctrl word
| 216 | [C308] (C308) | Bit 8 Com card ctrl word
| 217 | [C309] (C309) | Bit 9 Com card ctrl word
| 218 | [C310] (C310) | Bit 10 Com card ctrl word
| 219 | [C311] (C311) | Bit 11 Com card ctrl word
| 220 | [C312] (C312) | Bit 12 Com card ctrl word
| 221 | [C313] (C313) | Bit 13 Com card ctrl word
| 222 | [C314] (C314) | Bit 14 Com card ctrl word
| 223 | [C315] (C315) | Bit 15 Com card ctrl word
| 240 | [OL01] (OL01) | OL01
| 241 | [OL02] (OL02) | OL02
| 242 | [OL03] (OL03) | OL03
| 243 | [OL04] (OL04) | OL04
| 244 | [OL05] (OL05) | OL05
| 245 | [OL06] (OL06) | OL06
| 246 | [OL07] (OL07) | OL07
| 247 | [OL08] (OL08) | OL08
| 248 | [OL09] (OL09) | OL09
| 249 | [OL10] (OL10) | OL10
| 250 | [None] (GDL)
PSLIN | 0 | [No] (NO) | Not assigned
| 1 | [No drive flt] (FLT) | No drive flt
| 96 | [ch1 active] (FR1) | Command ch = ch 1
| 97 | [ch2 active] (FR2) | Command ch = ch 1B
| 100 | [ch1B active] (FR1B) | Command ch = ch 1B
| 98 | [ch1 active] (CD1) | Control ch. = Channel 1
| 99 | [ch2 active] (CD2) | Control ch. = Channel 2
| 128 | [Yes] (YES) | Yes
| 4 | [Freq.Th.att.] (FTA) | Freq. threshold reached
| 13 | [FreqTh.att.2] (F2A) | FreqTh.att.2
| 129 | [LI1] (LI1) | Logic input LI1
| 130 | [LI2] (LI2) | Logic input LI2
| 131 | [LI3] (LI3) | Logic input LI3
| 132 | [LI4] (LI4) | Logic input LI4
| 133 | [LI5] (LI5) | Logic input LI5
| 134 | [LI6] (LI6) | Logic input LI6
| 143 | [LAI1] (LAI1) | Logic input AI1
| 144 | [LAI2] (LAI2) | Logic input AI2
| 160 | [CD00] (CD00) | Bit 0 logic input ctrl word
| 161 | [CD01] (CD01) | Bit 1 logic input ctrl word
| 162 | [CD02] (CD02) | Bit 2 logic input ctrl word
| 163 | [CD03] (CD03) | Bit 3 logic input ctrl word
| 164 | [CD04] (CD04) | Bit 4 logic input ctrl word
| 165 | [CD05] (CD05) | Bit 5 logic input ctrl word
| 166 | [CD06] (CD06) | Bit 6 logic input ctrl word
| 167 | [CD07] (CD07) | Bit 7 logic input ctrl word
| 168 | [CD08] (CD08) | Bit 8 logic input ctrl word
| 169 | [CD09] (CD09) | Bit 9 logic input ctrl word
| 170 | [CD10] (CD10) | Bit10 logic input ctrl word
| 171 | [CD11] (CD11) | Bit11 logic input ctrl word
| 172 | [CD12] (CD12) | Bit12 logic input ctrl word
| 173 | [CD13] (CD13) | Bit13 logic input ctrl word
| 174 | [CD14] (CD14) | Bit14 logic input ctrl word
| 175 | [CD15] (CD15) | Bit15 logic input ctrl word
| 177 | [C101] (C101) | Bit 1 Modbus ctrl word
| 178 | [C102] (C102) | Bit 2 Modbus ctrl word
| 179 | [C103] (C103) | Bit 3 Modbus ctrl word
| 180 | [C104] (C104) | Bit 4 Modbus ctrl word
| 181 | [C105] (C105) | Bit 5 Modbus ctrl word
| 182 | [C106] (C106) | Bit 6 Modbus ctrl word
| 183 | [C107] (C107) | Bit 7 Modbus ctrl word
| 184 | [C108] (C108) | Bit 8 Modbus ctrl word
| 185 | [C109] (C109) | Bit 9 Modbus ctrl word
| 186 | [C110] (C110) | Bit 10 Modbus ctrl word
| 187 | [C111] (C111) | Bit 11 Modbus ctrl word
| 188 | [C112] (C112) | Bit 12 Modbus ctrl word
| 189 | [C113] (C113) | Bit 13 Modbus ctrl word
| 190 | [C114] (C114) | Bit 14 Modbus ctrl word
| 191 | [C115] (C115) | Bit 15 Modbus ctrl word
| 193 | [C201] (C201) | Bit 1 CANopen ctrl word
| 194 | [C202] (C202) | Bit 2 CANopen ctrl word
| 195 | [C203] (C203) | Bit 3 CANopen ctrl word
| 196 | [C204] (C204) | Bit 4 CANopen ctrl word
| 197 | [C205] (C205) | Bit 5 CANopen ctrl word
| 198 | [C206] (C206) | Bit 6 CANopen ctrl word
| 199 | [C207] (C207) | Bit 7 CANopen ctrl word
| 200 | [C208] (C208) | Bit 8 CANopen ctrl word
| 201 | [C209] (C209) | Bit 9 CANopen ctrl word
| 202 | [C210] (C210) | Bit 10 CANopen ctrl word
| 203 | [C211] (C211) | Bit 11 CANopen ctrl word
| 204 | [C212] (C212) | Bit 12 CANopen ctrl word
| 205 | [C213] (C213) | Bit 13 CANopen ctrl word
| 206 | [C214] (C214) | Bit 14 CANopen ctrl word
| 207 | [C215] (C215) | Bit 15 CANopen ctrl word
| 209 | [C301] (C301) | Bit 1 Com card ctrl word
| 210 | [C302] (C302) | Bit 2 Com card ctrl word
| 211 | [C303] (C303) | Bit 3 Com card ctrl word
| 212 | [C304] (C304) | Bit 4 Com card ctrl word
| 213 | [C305] (C305) | Bit 5 Com card ctrl word
| 214 | [C306] (C306) | Bit 6 Com card ctrl word
| 215 | [C307] (C307) | Bit 7 Com card ctrl word
| 216 | [C308] (C308) | Bit 8 Com card ctrl word
| 217 | [C309] (C309) | Bit 9 Com card ctrl word
| 218 | [C310] (C310) | Bit 10 Com card ctrl word
| 219 | [C311] (C311) | Bit 11 Com card ctrl word
| 220 | [C312] (C312) | Bit 12 Com card ctrl word
| 221 | [C313] (C313) | Bit 13 Com card ctrl word
| 222 | [C314] (C314) | Bit 14 Com card ctrl word
| 223 | [C315] (C315) | Bit 15 Com card ctrl word
| 240 | [OL01] (OL01) | OL01
| 241 | [OL02] (OL02) | OL02
| 242 | [OL03] (OL03) | OL03
| 243 | [OL04] (OL04) | OL04
| 244 | [OL05] (OL05) | OL05
| 245 | [OL06] (OL06) | OL06
| 246 | [OL07] (OL07) | OL07
| 247 | [OL08] (OL08) | OL08
| 248 | [OL09] (OL09) | OL09
| 249 | [OL10] (OL10) | OL10
PTCX | 0 | [No] (NO) | No management
| 1 | [Always] (AS) | Always
| 2 | [Power ON] (RDS) | Power ON
| 3 | [Motor ON] (RS) | Motor ON
QSTD | 2 | [None] (FST2)
| 6 | [None] (FST6)
RDS | 0 | [Auto] (AUTO) | Auto detected
| 1 | [10M. full] (10F) | 10Mbps full duplex
| 2 | [10M. half] (10H) | 10Mbps half duplex
| 3 | [100M. full] (100F) | 100Mbps full duplex
| 4 | [100M. half] (100H) | 100Mbps half duplex
RPR | 0 | [No] (NO) | No
| 1 | [reset kWh] (APH) | reset kWh counters
| 2 | [rst. runtime] (RTH) | Operate time reset - zero
| 3 | [rst runtim I] (RTHI) | Reset runtime internal
| 4 | [rst. P On t.] (PTH) | Reset power on time
| 64 | [Reset all ] (ALL) | Reset all counters
RPT | 0 | [Linear] (LIN) | Linear ramp
| 1 | [S ramp] (S) | S-Ramp
| 2 | [U ramp] (U) | U-Ramp
| 3 | [Customized] (CUS) | Ramp customized
RSD | 0 | [No] (NO) | No
| 1 | [Drive estim.] (DRI) | Drive estimation
| 2 | [Ext. sensor] (PES) | Extern weight sensor
SCS | 0 | [No] (NO) | No
| 1 | [Config 0] (STR0) | Save configuration 0
| 2 | [Config 1] (STR1) | Save configuration 1
| 3 | [Config 2] (STR2) | Save configuration 2
SFT | 1 | [SFR type 1] (HF1) | Switch.frequency type 1
| 2 | [SFR type 2] (HF2) | Switch.frequency type 2
SFTY | 0 | [Standard] (STD) | Standard drive
| 1 | [Safe] (SAFE) | Safe drive
SLSS | 0 | [Not config.] (NO) | Not configured
| 1 | [Idle] (IDLE) | No activated
| 2 | [Safe ramp] (SS1) | Safe ramp
| 3 | [Spd limited] (SLS) | Speed limited
| 4 | [Safe stop] (STO) | Safe stop
| 5 | [Fault] (FLT) | Fault
| 6 | [SLS wait] (WAIT)
| 7 | [SLS Start] (STRT)
SLT | 0 | [None] (TYP1)
| 1 | [None] (TYP2)
| 2 | [None] (TYP3)
| 3 | [None] (TYP4)
| 4 | [None] (TYP5)
| 5 | [None] (TYP6)
SMOT | 0 | [No info.] (NO) | No information
| 1 | [Low salient] (LLS) | Low saliency
| 2 | [Med salient] (MLS) | Medium saliency
| 3 | [High salient] (HLS) | High saliency
SMSA | 0 | [None] (NO)
| 1 | [None] (YES)
SMSS | 0 | [None] (NO)
| 1 | [None] (SMS)
| 2 | [None] (FTI)
| 3 | [None] (FTO)
SOP | 6 | [6 µs] (6) | 6 µs
| 8 | [8 µs] (8) | 8 µs
| 10 | [10 µs] (10) | 10 µs
SPIG | 0 | [Stop] (STOP) | Stop
| 1 | [Ignore] (IGN) | Ignore
SPSL | 0 | [None] (NO)
| 1 | [None] (L34)
| 2 | [None] (L56)
| 3 | [None] (L3PW)
| 4 | [None] (PWRM)
SPST | 0 | [Stop] (STOP) | Stop
| 1 | [Start] (STRT) | Start
SS1S | 0 | [Not config.] (NO) | Not configured
| 1 | [Idle] (IDLE) | No activated
| 2 | [Safe ramp] (SS1) | Safe ramp
| 3 | [Safe stop] (STO) | Safe stop
| 4 | [Fault] (FLT) | Fault
SSRU | 0 | [None] (1H)
| 1 | [None] (10H)
| 2 | [None] (100H)
STOS | 0 | [Idle] (IDLE) | No activated
| 1 | [Safe stop] (STO) | Safe stop
| 2 | [Fault] (FLT) | Fault
STP | 0 | [No] (NO) | Freewheel stop with fault
| 1 | [DC Maintain] (MMS) | Maintain DC bus
| 2 | [Ramp stop] (RMP) | Stop with valid ramp
| 4 | [Lock-out] (LNF) | Freewheel stop no fault
STR | 0 | [No] (NO) | No save
| 1 | [RAM] (RAM) | Save to RAM
| 2 | [EEprom] (EEP) | Save to EEPROM
STT | 0 | [Ramp stop] (RMP) | Stop on decel. ramp
| 1 | [Fast stop] (FST) | Fast stop
| 2 | [Freewheel] (NST) | Freewheel stop
| 3 | [DC injection] (DCI) | DC injection stop
STUN | 0 | [Default] (TAB) | Default
| 1 | [Measure] (MEAS) | Measure
| 2 | [Custom] (CUS) | Custom
TBR | 0 | [Not config.] (NO) | Not configured
| 4 | [Automatic] (AUTO) | Automatic
| 8 | [300 bps] (300) | 300 bps
| 12 | [600 bps] (600) | 600 bps
| 16 | [1.2 Kbps] (1200) | 1.2 Kbps
| 20 | [2.4 Kbps] (2400) | 2.4 Kbps
| 24 | [4.8 Kbps] (4800) | 4.8 Kbps
| 28 | [9.6 Kbps] (9600) | 9.6 Kbps
| 30 | [10 Kbps] (10000) | 10 Kbps
| 32 | [19.2 Kbps] (19200) | 19.2 Kbps
| 34 | [20 Kbps] (20000) | 20 Kbps
| 35 | [28.8 Kbps] (28800) | 28.8 Kbps
| 36 | [38.4 Kbps] (38400) | 38.4 Kbps
| 37 | [45.45 Kbps] (45450) | 45.45 Kbps
| 38 | [50 Kbps] (50000) | 50 Kbps
| 40 | [57.6 Kbps] (57600) | 57.6 Kbps
| 42 | [93.75 Kbps] (93750) | 93.75 Kbps
| 44 | [100 Kbps] (100K) | 100 Kbps
| 48 | [115.2 Kbps] (115K2) | 115.2 Kbps
| 52 | [125 Kbps] (125K) | 125 Kbps
| 53 | [156 Kbps] (156K) | 156 Kbps
| 54 | [187.5 Kbps] (187K5) | 187.5 Kbps
| 56 | [230.4 Kbps] (230K4) | 230.4 Kbps
| 60 | [250 Kbps] (250K) | 250 Kbps
| 64 | [460.8 Kbps] (460K8) | 460.8 Kbps
| 68 | [500 Kbps] (500K) | 500 Kbps
| 69 | [625 Kbps] (625K) | 625 Kbps
| 70 | [800 Kbps] (800K) | 800 Kbps
| 72 | [921.6 Kbps] (921K6) | 921.6 Kbps
| 76 | [1 Mbps] (1M) | 1 Mbps
| 80 | [1.5 Mbps] (1M5) | 1.5 Mbps
| 81 | [2.5 Mbps] (2M5) | 2.5 Mbps
| 82 | [3 Mbps] (3M) | 3 Mbps
| 83 | [6 Mbps] (6M) | 6 Mbps
| 84 | [10 Mbps] (10M) | 10 Mbps
| 86 | [5 Mbps] (5M) | 5 Mbps
| 88 | [12 Mbps] (12M) | 12 Mbps
| 92 | [100 Mbps] (100M) | 100 Mbps
TCC | 0 | [2 wire] (2C) | 2-wire control
| 1 | [3 wire] (3C) | 3-wire control
TCT | 0 | [Level] (LEL) | Level triggered
| 1 | [Transition] (TRN) | Edge triggered
| 2 | [Fwd priority] (PFO) | Level trigger fwd priority
THT | 0 | [No] (NO) | No thermal protection
| 1 | [Self cooled] (ACL) | Self cooled motor
| 2 | [Force-cool] (FCL) | Force cooled motor
TUNU | 0 | [No] (NO) | No
| 1 | [Therm mot] (TM) | Use the motor thermal evolution
| 2 | [Cold tun] (CT) | Use the cold tune values
URES | 20 | [200V ac] (200) | 200V ac
| 22 | [220V ac] (220) | 220V ac
| 23 | [230V ac] (230) | 230V ac
| 24 | [240V ac] (240) | 240V ac
| 38 | [380V ac] (380) | 380V ac
| 40 | [400V ac] (400) | 400V ac
| 44 | [440V ac] (440) | 440V ac
| 46 | [460V ac] (460) | 460V ac
| 50 | [500V ac] (500) | 500V ac
| 53 | [None] (525)
| 60 | [600V ac] (600) | 600V ac
| 254 | [Lexium] (LHM) | Lexium compatibility level
USB | 0 | [Std fault] (0) | Standard fault
| 1 | [Flt wo relay] (1) | Fault without Relay action
| 2 | [Alarm] (2) | Alarm only
VCAL | 0 | [No] (NO) | Unknown drive rate volt.
| 1 | [100-120(1)] (110M) | 100-120 V single phase
| 2 | [100-120(3)] (110T) | 100-120 V three phase
| 3 | [200-240(1)] (220M) | 200-240 V single phase
| 4 | [200-240(3)] (220T) | 200-240 V three phase
| 5 | [380-500(1)] (480M) | 380-500 V single phase
| 6 | [380-500(3)] (480T) | 380-500 V three phase
| 7 | [525-600(1)] (690M) | 525-600 V single phase
| 8 | [525-600(3)] (690T) | 525-600 V three phase
| 9 | [500 / 600V] (600M) | 600V single-phase
| 10 | [500 / 600V] (600T) | 600V three-phase

## Registers
CMI |  | Bit 0 | Factory setting command (active at 1).
|  | Bit 1 | Save configuration to EEPROM non-volatile memory command (active at 1).
This Bit automatically changes to 0 after the request is taken into account. The command is only active if the drive is stopped, and not in "5-Operation enabled" state.
Note: If CMI is a periodic network variable, the PLC program must write it to 0 after the first request is taken into account. The life of the EEPROM memory is limited to 100,000 write operations.
Note: If the motor or configuration switching function is active, the configuration in the RAM is saved to the EEPROM in the configuration designated by [Config. Active] (CnFS).
|  | Bit 2 | Reserved (= 0).
|  | Bit 3 | Reserved (= 0).
|  | Bit 4 | Reserved (= 0).
|  | Bit 5 | Reserved (= 0).
|  | Bit 6 | Reserved (= 0).
|  | Bit 7 | Reserved (= 0).
|  | Bit 8 | Reserved (= 0).
|  | Bit 9 | Definition of the frequency reference (LFr) and output frequency (rFr) unit:
= 0: 0.1 Hz
= 1: Standardized value 16 signed bits based on the maximum frequency. The value 32767 corresponds to [Max frequency] (tFr). The default value of [Max frequency] (tFr) is 60 Hz, and the resolution is then approximately 0.0018 Hz.
This function has no effect on the speed reference (LFrd) or the output speed (rFrd).
|  | Bit 10 | Reserved (= 0).
|  | Bit 11 | Reserved (= 0).
|  | Bit 12 | Reserved (= 0).
|  | Bit 13 | Reserved (= 0).
|  | Bit 14 | Reserved (= 0).
|  | Bit 15 | Parameter consistency check
= 0: The check is activated. Each time a parameter is written, the drive checks the relationship between the written parameter and the configuration in the drive. For example, the [High speed] (HSP) parameter must be less than [Max frequency] (tFr).
= 1: The check is deactivated. The drive is locked in stop mode. In this drive state, the configuration can be written parameter by parameter and the drive does not modify the values that are written.
The switch from 1 to 0 triggers a calculation of the consistency of the configuration. Some parameters can be modified automatically by the drive.
CMD | Possible values in CiA402 profile, separate or not separate mode:
CMP0 |  | Bit 0 | Switch on/Contactor command.
CMP1 |  | Bit 1 | Disable voltage/Authorization to supply AC power.
CMP2 |  | Bit 2 | Quick stop.
CMP3 |  | Bit 3 | Enable operation/Run command.
CMP4 |  | Bit 4 | Reserved (set to 0).
CMP5 |  | Bit 5 | Reserved (set to 0).
CMP6 |  | Bit 6 | Reserved (set to 0).
CMP7 |  | Bit 7 | Fault reset/error cleared on transition 0 to 1 .
CMP8 |  | Bit 8 | Halt Stop according to the [Type of stop] (Stt) parameter without leaving the Operation enabled state.
|  | Bit 9 | Reserved (set to 0).
|  | Bit 10 | Reserved (set to 0).
|  | Bit 11 to 15 | Can be assigned to commands.
Possible values in the IO profile on state command [2 wire] (2C).
|  | Bit 0 | Forward (on state) command
= 0: No forward command
= 1: Forward command
The assignment of Bit 0 cannot be modified. It corresponds to the assignment of the terminals. It can be switched. Bit 0 (Cd00) is only active if the channel of this control word is active.
|  | Bit 1 to 15 | Can be assigned to commands.
Possible values in the IO profile on edge command [3 wire] (3C).
|  | Bit 0 | Stop (run authorization).
= 0: Stop
= 1: Run is authorized on a forward or reverse command
|  | Bit 1 | Forward (on 0 to 1 rising edge) command.
The assignment of Bits 0 and 1 cannot be modified. It corresponds to the assignment of the terminals. It can be switched. Bits 0 (Cd00) and 1 (Cd01) are only active if the channel of this control word is active.
|  | Bit 2 to 15 | can be assigned to commands.
ETA | Possible values in CiA402 profile, separate or not separate mode:
EP0 |  | Bit 0 | = 1: "Ready to switch on", awaiting power section line supply
EP1 |  | Bit 1 | = 1: "Switched on", ready
EP2 |  | Bit 2 | = 1: "Operation enabled", running
EP3 |  | Bit 3 | = 1: Fault detection
EP4 |  | Bit 4 | "Voltage enabled", power part connected to supply mains
EP5 |  |  | = 0: Power part not connected to supply mains
EP6 |  |  | = 1: Power part connected to supply mains
EP7 |  |  | When the drive is powered by the power section only, this bit is always at 1.
EP8 |  | Bit 5 | Bit 5: = 0: Quick stop
ETAD |  | Bit 6 | Bit 6: = 1: "Switched on disabled", power section line supply locked
|  | Bit 7 | Bit 7: Warning
= 0: No warning
= 1: Warning active
|  | Bit 8 | Bit 8: Reserved (= 0)
|  | Bit 9 | Bit 9: Remote: command or reference via fieldbus
= 0: Command or reference given via the graphic display terminal or remote display terminal
= 1: Command or reference via fieldbus
|  | Bit 10 | Bit 10: Target reference reached
= 0: The reference is not reached
= 1: The reference has been reached
When the drive is in speed mode, this is the reference frequency.
|  | Bit 11 | Bit 11: "Internal limit active", reference outside limits
= 0: The reference is within the limits
= 1: The reference is not within the limits
When the drive is in speed mode, the limits are defined by the [Low speed] (LSP) and [High speed] (HSP) parameters.
|  | Bit 12 | Bit 12: Reserved (= 0)
|  | Bit 13 | Bit 13: Reserved (= 0)
|  | Bit 14 | Bit 14: "Stop key", STOP via stop key
= 0: STOP key not active
= 1: Stop triggered by the STOP key on the graphic display terminal or the remote display terminal
|  | Bit 15 | Bit 15: "Direction", direction of rotation
= 0: Forward rotation at output
= 1: Reverse rotation at output
The combination of Bits 0, 1, 2, 4, 5 and 6 defines the state in the DSP 402 state chart (refer to fieldbus manuals).
ETI |  | Bit 0 | = 1: Access to the EEPROM non-volatile memory in progress
IP0 |  | Bit 1 | = 0: No parameter consistency check
IP1 |  |  | = 1: Parameter consistency check
IP2 |  | Bit 2 | = 0: The drive is not in operating state "Fault" or in operating state "Fault" and the error is active
IP3 |  |  | = 1: The drive is in operating state "Fault" and the error is no longer active (not reset))
IP4 |  | Bit 3 | Bit 3: Reserved (= 0).
IP5 |  | Bit 4 | = 1: The drive is in speed mode
IP6 |  | Bit 5 | = 1: DC injection active
IP7 |  | Bit 6 | = 0: Drive in steady state
IP8 |  |  | = 1: Drive in transient state
|  | Bit 7 | = 1: Motor thermal state threshold reached for the active motor
|  | Bit 8 | = 1: DC bus overvoltage
|  | Bit 9 | = 1: Acceleration active
|  | Bit 10 | = 1: Deceleration active
|  | Bit 11 | = 1: Current limit active
|  | Bit 12 | = 1: Fast stop active
|  | Bit 13 to 14 | bit 13 = 0 and bit 14 = 0: Drive controled by terminal
bit 13 = 1 and bit 14 = 0: Drive controled by remote keypad
bit 13 = 0 and bit 14 = 1: Drive controled by Modbus
bit 13 = 1 and bit 14 = 1: Drive controled by CANopen or the network card
|  | Bit 15 | = 0: Forward operation applied before the ramp
= 1: Reverse operation applied before the ramp
CRC |  | Bit 0 | = 1 : Terminal board
|  | Bit 1 | = 1 : Local keypad
|  | Bit 2 | = 1 : Deported keypad
|  | Bit 3 | = 1 : Modbus
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | = 1 : CANopen
|  | Bit 7 | = 1 : Terminal up-Down speed
|  | Bit 8 | = 1 : Deported keypad up-down speed
|  | Bit 9 | = 1 : COM option board
|  | Bit 10 | = 1 : APP option board
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | = 1 : Indus
|  | Bit 15 | = 1 : PowerSuite
CCC |  | Bit 0 | = 1 : Terminal board
|  | Bit 1 | = 1 : Local keypad
|  | Bit 2 | = 1 : Deported keypad
|  | Bit 3 | = 1 : Modbus
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | = 1 : CANopen
|  | Bit 7 | = 1 : Terminal up-Down speed
|  | Bit 8 | = 1 : Deported keypad up-down speed
|  | Bit 9 | = 1 : COM option board
|  | Bit 10 | = 1 : APP option board
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | = 1 : Indus
|  | Bit 15 | = 1 : PowerSuite
IL1R |  | Bit 0 | "LI1" logic inputs real image
|  | Bit 1 | "LI2" logic inputs real image
|  | Bit 2 | "LI3" logic inputs real image
|  | Bit 3 | "LI4" logic inputs real image
|  | Bit 4 | "LI5" logic inputs real image
|  | Bit 5 | "LI6" logic inputs real image
|  | Bit 6 | "AI1" as logic input real image
|  | Bit 7 | "AI2" as logic input real image
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
OL1R |  | Bit 0 | "R1" relay real image
|  | Bit 1 | "R2" relay real image
|  | Bit 2 | Reserved
|  | Bit 3 | Reserved
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | "L01" logic outputs real image
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
CIC |  | Bit 0 | = 1: Change of rating.
|  | Bit 1 | = 1: The fielbus module has been added.
|  | Bit 2 | = 1: The fielbus module has been removed.
|  | Bit 3 | = 1: Loaded config invalid.
|  | Bit 4 | = 1: The fielbus module has been changed.
|  | Bit 5 | Reserved (=0).
|  | Bit 6 | Reserved (=0).
|  | Bit 7 | Reserved (=0).
|  | Bit 8 | = 1: The IO module has been added.
|  | Bit 9 | = 1: The IO module has been removed.
|  | Bit 10 | = 1: The IO module has been changed.
|  | Bit 11 | = 1: The encoder module has been added.
|  | Bit 12 | = 1: The encoder module has been removed.
|  | Bit 13 | = 1: The encoder module has been changed.
|  | Bit 14 | = 1: The control board has been changed.
If one of these events occurs, the drive will trigger an error [Invalid configiguration] (CFI) and then automatically restore the factory settings.
CRP0 | Bit 0 to Bit 7: Active command channels
CRP1 |  |  | =0 : The terminal board is the active channel.
CRP2 |  |  | =1 : The local keypad is the active channel.
CRP3 |  |  | =2 : The remote keypad is the active channel.
CRP4 |  |  | =3 : Modbus is the active channel.
CRP5 |  |  | =4 : Reserved
CRP6 |  |  | =5 : Reserved
CRP7 |  |  | =6 : CANopen is the active channel.
CRP8 |  |  | =7 : The terminals are the active channel in the +/- speed reference.
=8 : The remote keypad is the active channel (up-down speed)
=9 : The fieldbus module is the active channel.
=10 : Reserved
=11 : Reserved
=12 : Reserved
=13 : Reserved
=14 : Reserved
=15 : SoMove software is the active channel.
Bit 8 to Bit 15: Active reference channels
=0 : The terminals are the active channel via an analog input.
=1 : The local keypad is the active channel.
=2 : The remote keypad is the active channel.
=3 : Modbus is the active channel.
=4 : Reserved
=5 : Reserved
=6 : CANopen is the active channel.
=7 : The terminals are the active channel in the +/- speed reference.
=8 : The remote keypad is the active channel (up-down speed)
=9 : The fieldbus module is the active channel.
=10 : Reserved
=11 : Reserved
=12 : Reserved
=13 : Reserved
=14 : Reserved
=15 : SoMove software is the active channel.
FRY |  | Bit 0 | = 1 : All parameters
|  | Bit 1 | = 1 : Drive configuration
|  | Bit 2 | Reserved
|  | Bit 3 | = 1 : Motor parameters
|  | Bit 4 | = 1 : Communication menu
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | = 1 : Display menu
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved (Bit15 = 1 : Communication option parameters)
EWE |  | Bit 0 | = 1 : Enable Web
|  | Bit 1 | = 1 : Enable Email
IL1I |  | Bit 0 | "LI1" logic inputs physical image
|  | Bit 1 | "LI2" logic inputs physical image
|  | Bit 2 | "LI3" logic inputs physical image
|  | Bit 3 | "LI4" logic inputs physical image
|  | Bit 4 | "LI5" logic inputs physical image
|  | Bit 5 | "LI6" logic inputs physical image
|  | Bit 6 | "AI1" as logic inputs physical image
|  | Bit 7 | "AI2" as logic inputs physical image
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
LRS1 |  |  | _(000_NO) Bit0 : Reserved
_(001_FLT) Bit1 = 1 : Drive fault
_(002_RUN) Bit2 = 1 : Drive running
_(003_OCC) Bit3 = 1 : Downstreamcontactor running
_(004_FTA) Bit4 = 1 : Motor frequency threshold (FTD) reached
_(005_FLA) Bit5 = 1 : High Speed (HSP) reached
_(006_CTA) Bit6 = 1 : Motor current threshold (CTD) reached
_(007_SRA) Bit7 = 1 : Frequency reference reached
_(008_TSA) Bit8 = 1 : Motor thermal threshold (TTD) reached
_(009_BLC) Bit9 = 1 : Braking sequence active
_(010_PEE) Bit10 = 1 : PID error
_(011_PFA) Bit11 = 1 : PID feedback alarm
_(012) Bit12 : Reserved
_(013_F2A) Bit13 = 1 : Second frequency threshold (F2D) reached
_(014_TAD) Bit14 = 1 : Drive thermal threshold reached
_(015_TRC) Bit15 = 1 : Traverse control running
LRS2 |  |  | _(016) Bit0 : Reserved
_(017) Bit1 : Reserved
_(018) Bit2 : Reserved
_(019) Bit3 : Reserved
_(020) Bit4 : Reserved
_(021_ULA) Bit5 = 1 : Undeload alarm
_(022_OLA) Bit6 = 1 : Overload alarm
_(023) Bit7 : Reserved
_(024) Bit8 : Reserved
_(025) Bit9 : Reserved
_(026) Bit10 : Reserved
_(027_RSDA) Bit11 : TBD
_(028_TTHA) Bit12 = 1 : High torque threshold
_(029_TTLA) Bit13 = 1 : Low torque threshold
_(030_MFRD) Bit14 = 1 : Run Forward
_(031_MRRS) Bit15 = 1 : Run Reverse
LRS3 |  |  | _(032_RFC) Bit0 = 0 : Reference channel 1, 1 : Reference channel 2
_(033_CCS) Bit1 = 0 : Command channel 1, 1 : Command channel 2
_(034_RP2) Bit2 = 1 : Ramp switching active
_(035_CL2) Bit3 = 1 : Current limitation switching active
_(036) Bit4 : Reserved
_(037_TS2) Bit5 = 1 : Motor 2 thermal threshold (TTD2) reached
_(038_TS3) Bit6 = 1 : Motor 3 thermal threshold (TTD3) reached
_(039) Bit7 : Reserved
_(040_EPR) Bit8 = 1 : External Power Present
_(041_SLM) Bit9 = 1 : Sleeping Mode active
_(042) Bit10 : Reserved
_(043) Bit11 : Reserved
_(044) Bit12 : Reserved
_(045) Bit13 : Reserved
_(046) Bit14 : Reserved
_(047_ATS) Bit15 = 1 : Actual torque sign
LRS4 |  |  | _(048_CNF0) Bit0 = 1 : Configuration 0 active
_(049_CNF1) Bit1 = 1 : Configuration 1 active
_(050_CNF2) Bit2 = 1 : Configuration 2 active
_(051) Bit3 : Reserved
_(052_CFP1) Bit4 = 1 : Parameter set 1 active
_(053_CFP2) Bit5 = 1 : Parameter set 2 active
_(054_CFP3) Bit6 = 1 : Parameter set 3 active
_(055) Bit7 : Reserved
_(056_PWR) Bit8 = 1 : Power removed
_(057_FLU) Bit9 = 1 : Fluxing in progress
_(058_FLX) Bit10 = 1 : Motor fluxed
_(059_IDC) Bit11 = 1 : DC injection running
_(060_CLI) Bit12 = 1 : Current limitation running
_(061_ACC) Bit13 = 1 : Product in acceleration
_(062_DEC) Bit14 = 1 : Product in deceleration
_(063_FST) Bit15 = 1 : Fast stop in progress
LRS5 |  |  | _(064_DBL) Bit0 = 1 : DC bus loaded
_(065_BRS) Bit1 = 1 : Braking activated
_(066_PRM) Bit2 = 1 : Power removed
_(067_AUTO) Bit3 = 1 : Automatic restart attempts in progress
_(068_TUN) Bit4 = 1 : Autotune in progress
_(069_CTL) Bit5 = 1 : Controlled stop in progress
_(070_OBR) Bit6 = 1 : Adapted deceleration in progress
_(071_SOC) Bit7 = 1 : Stand by output cut in progress
_(072_FQLA) Bit8 = 1 : Frequency level reached status
_(073_LLC) Bit9 = 1 : Line contactor activated
_(074_TUD) Bit10 = 1 : Autotune complete
_(075_EEP) Bit11 = 1 : Eeprom writing in progress
_(076_EED) Bit12 = 1 : Eeprom writing complete
_(077_MCP) Bit13 = 1 : Motor current present
_(078_LSA) Bit14 = 1 : Limit switch function activated
_(079_DLDA) Bit15 : TBD
LRS6 |  |  | _(080_AG1) Bit0 = 1 : Alarm Group 1
_(081_AG2) Bit1 = 1 : Alarm Group 2
_(082_AG3) Bit2 = 1 : Alarm Group 3
_(083) Bit3 : Reserved
_(084) Bit4 : Reserved
_(085_PLA) Bit5 = 1 : PTCL Alarm
_(086) Bit6 : Reserved
_(087_EFA) Bit7 = 1 : External fault alarm
_(088_USA) Bit8 = 1 : Undervoltage alarm
_(089_UPA) Bit9 = 1 : Undervoltage prevention Alarm
_(090) Bit10 : Reserved
_(091_THA) Bit11 = 1 : Transistor heating alarm
_(092) Bit12 : Reserved
_(093) Bit13 : Reserved
_(094) Bit14 : Reserved
_(095_SSA) Bit15 = 1 : Torque current limitation alarm
LRS7 |  |  | _(096_FR1) Bit0 = 1 : Reference channel = channel 1 (for RFC)
_(097_FR2) Bit1 = 1 : Reference channel = channel 2 (for RFC)
_(098_CD1) Bit2 = 1 : Command channel = channel 1 (for CCS)
_(099_CD2) Bit3 = 1 : Command channel = channel 2 (for CCS)
_(100_FR1B) Bit4 = 1 : Reference channel = channel 1B (for RFC)
_(101_EBO) Bit5 = 1 : End of bobbin
_(102_TSY) Bit6 = 1 : Traverse control synchronization counter wobble
_(103) Bit7 : Reserved
_(104_TJA) Bit8 = 1 : Thermal junction alarm
_(105) Bit9 : Reserved
_(106) Bit10 : Reserved
_(107_AP3) Bit11 = 1 : AI3 4-20 mA loss alarm
_(108) Bit12 : Reserved
_(109) Bit13 : Reserved
_(110) Bit14 : Reserved
_(111) Bit15 : Reserved
LRS8 |  |  | _(112_SAF) Bit0 = 1 : Stop Switch in Forward(SAF) activated
_(113_SAR) Bit1 = 1 : Stop Switch in Reverse(SAR) activated
_(114_NOFW) Bit2 = 1 : Forward impossible (Stop Switch in Forward(SAF) memorized or activated)
_(115_NORV) Bit3 = 1 : Reverse impossible (Stop Switch in Reverse(SAR) memorized or activated)
_(116) Bit4 : Reserved
_(117) Bit5 : Reserved
_(118) Bit6 : Reserved
_(119) Bit7 : Reserved
_(120) Bit8 : Reserved
_(121_FLO) Bit9 = 1 : force local mode activated
_(122) Bit10 : Reserved
_(123) Bit11 : Reserved
_(124) Bit12 : Reserved
_(125) Bit13 : Reserved
_(126) Bit14 : Reserved
_(127_RDY) Bit15 = 1 : Product ready to start
S001 |  | Bit 0 | Reserved
|  | Bit 1 | Reserved
|  | Bit 2 | Reserved
|  | Bit 3 | Reserved
|  | Bit 4 | Reserved
|  | Bit 5 | TB100MS : Clock bit : period 100ms, duty cycle 50%
|  | Bit 6 | TB1SEC : Clock bit : period 1s, duty cycle 50%
|  | Bit 7 | TB1MIN : Clock bit : period 1min, duty cycle 50%
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | 1RSTSCANRUN : FB is executing its 1rst cycle since last RUN.
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
S002 |  | Bit 0 | Reserved
|  | Bit 1 | Reserved
|  | Bit 2 | Reserved
|  | Bit 3 | Reserved
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | OPTION_OK
|  | Bit 12 | CANOPEN_OK
|  | Bit 13 | MODBUS_OK
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
S006 |  | Bit 0 | Reserved
|  | Bit 1 | Reserved
|  | Bit 2 | Reserved
|  | Bit 3 | Reserved
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | USRMWSAVE : Users variable save request (Save configuration)
|  | Bit 15 | Reserved
SAF1 |  |  | APP Safety fault register
|  | Bit 0 | = 1 : CoT : PWRM consistency fault
|  | Bit 1 | = 1 : DSP : Safe parameters fault
|  | Bit 2 | = 1 : ATAP : App auto test fault (details: SF00)
|  | Bit 3 | = 1 : DSFIP : Diagnostic check of safe function activation
|  | Bit 4 | = 1 : LICT : Logical inputs diagnostic fault (details: SF01)
|  | Bit 5 | = 1 : EXTEND: Extended fault (details: SF04)
|  | Bit 6 | = 1 : WDM1 : App watchdog management fault (details: SF02/SF07)
|  | Bit 7 | = 1 : MC : Motor control fault
|  | Bit 8 | = 1 : ISL : Internal Serial Link Core fault
|  | Bit 9 | = 1 : LIA : Logical Input activation fault (details: SF03)
|  | Bit 10 | = 1 : STO : Safe Torque Off fault (details: SF04)
|  | Bit 11 | = 1 : APPINT: App safety interface fault
|  | Bit 12 | = 1 : SS1 : Safe Stop 1 fault (details: SF05)
|  | Bit 13 | = 1 : SLS : Safely Limited Speed fault (details: SF06)
|  | Bit 14 | = 1 : MOTOR : Motor data fault
|  | Bit 15 | = 1 : CISL : Internal Serial Link Data Flow fault (partial details: SF11)
SAF2 |  |  | MC Safety fault register
|  | Bit 0 | = 1 : Consistency Stator Frequency check fault
|  | Bit 1 | = 1 : Stator Frequency Estimation fault
|  | Bit 2 | = 1 : Motor control watchdog management is active (details: SF08)
|  | Bit 3 | = 1 : Motor control hardware watchdog is active
|  | Bit 4 | = 1 : Motor control auto test has detected an error (details: SF09)
|  | Bit 5 | = 1 : Chain testing detected error
|  | Bit 6 | = 1 : Internal serial link core detected error
|  | Bit 7 | = 1 : Direct short-circuit detected error (details: SF10)
|  | Bit 8 | = 1 : PWM driver detected error
|  | Bit 9 | = 1 : GDL internal detected error
|  | Bit 10 | : Reserved
|  | Bit 11 | = 1 : Application interface has detected an error of the safety functions
|  | Bit 12 | : Reserved
|  | Bit 13 | : Reserved
|  | Bit 14 | = 1 : Motor data is corrupted
|  | Bit 15 | = 1 : Internal serial link data flow detected error (partial details: SF11)
SF00 |  |  | Safety App Auto Test fault register
|  | Bit 0 | Reserved
|  | Bit 1 | = 1 : Ram stack overflow
|  | Bit 2 | = 1 : Ram address integrity error
|  | Bit 3 | = 1 : Ram data access error
|  | Bit 4 | = 1 : Flash Checksum Error
|  | Bit 5 | Reserved
|  | Bit 6 | = 1 : Consistency check - ram address variables
|  | Bit 7 | = 1 : Consistency check - ram data access variables
|  | Bit 8 | = 1 : Consistency check - DMA channels variables
|  | Bit 9 | = 1 : Fast task overflow
|  | Bit 10 | = 1 : Slow task overflow
|  | Bit 11 | = 1 : App task overflow
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | = 1 : PWRM line is not activated during initialization phase
|  | Bit 15 | = 1 : Hardware WD is not running after initialization
SF01 |  |  | Safety LI Diagnostic fault register
|  | Bit 0 | = 1 : Management - state machine error
|  | Bit 1 | = 1 : Data required for test management are corrupted
|  | Bit 2 | = 1 : Channel selection error
|  | Bit 3 | = 1 : Testing - state machine error
|  | Bit 4 | = 1 : Test request is corrupted
|  | Bit 5 | = 1 : Pointer to test method is corrupted
|  | Bit 6 | = 1 : Incorrect test action provided
|  | Bit 7 | = 1 : Error in results collecting
|  | Bit 8 | = 1 : LI3 is defective. Cannot activate safe function
|  | Bit 9 | = 1 : LI4 is defective. Cannot activate safe function
|  | Bit 10 | = 1 : LI5 is defective. Cannot activate safe function
|  | Bit 11 | = 1 : LI6 is defective. Cannot activate safe function
|  | Bit 12 | = 1 : Test sequence updated while a diagnostic is in progress
|  | Bit 13 | = 1 : Error in test pattern management
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
SF02 |  |  | Safety App Watchdog Management fault register
|  | Bit 0 | = 1 : Fast task fault
|  | Bit 1 | = 1 : Slow task fault
|  | Bit 2 | = 1 : App task fault
|  | Bit 3 | = 1 : Background task fault
|  | Bit 4 | = 1 : Safety fast task/input fault
|  | Bit 5 | = 1 : Safety slow task/input fault
|  | Bit 6 | = 1 : Safety app task/input fault
|  | Bit 7 | = 1 : Safety app task/treatment fault
|  | Bit 8 | = 1 : Safety background task fault
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
SF03 |  |  | Safety LI Activation fault register
|  | Bit 0 | = 1 : Debounce time out
|  | Bit 1 | = 1 : Input not consistent
|  | Bit 2 | = 1 : Consistency check - state machine error
|  | Bit 3 | = 1 : Consistency check - debounce timeout corrupted
|  | Bit 4 | = 1 : Response time data error
|  | Bit 5 | = 1 : Response time corrupted
|  | Bit 6 | = 1 : Undefined consumer queried
|  | Bit 7 | = 1 : Configuration error
|  | Bit 8 | = 1 : Inputs are not in nominal mode
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
SF04 |  |  | Safe Torque Off fault register
|  | Bit 0 | = 1 : No signal configured
|  | Bit 1 | = 1 : State machine error
|  | Bit 2 | = 1 : Internal data error
|  | Bit 3 | Reserved
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | =1 : SMS SAFF Overspeed
|  | Bit 9 | =1 : SMS SAFF Internal
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | =1 : SFO SAFF Internal
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
SF05 |  |  | Safe Stop 1 fault register
|  | Bit 0 | = 1 : State machine error
|  | Bit 1 | = 1 : Motor speed sign changed during stop
|  | Bit 2 | = 1 : Motor speed reached trip area
|  | Bit 3 | = 1 : Theoretical motor speed corrupted
|  | Bit 4 | = 1 : Unauthorized configuration
|  | Bit 5 | = 1 : Theoretical motor speed computation error
|  | Bit 6 | Reserved
|  | Bit 7 | = 1 : Speed sign check: consistency error
|  | Bit 8 | = 1 : Internal SS1 request corrupted
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
SF06 |  |  | Safely Limited Speed fault register
|  | Bit 0 | = 1 : State machine error
|  | Bit 1 | = 1 : Motor speed sign changed during limitation
|  | Bit 2 | = 1 : Motor speed reached trip area
|  | Bit 3 | = 1 : Data corruption
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
SF07 |  |  | Safety App Watchdog Management fault register
|  | Bit 0 | Reserved
|  | Bit 1 | Reserved
|  | Bit 2 | Reserved
|  | Bit 3 | Reserved
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
SF08 |  |  | Safety Mc Watchdog Management fault register
|  | Bit 0 | = 1 : PWM task fault
|  | Bit 1 | = 1 : Fixed task fault
|  | Bit 2 | = 1 : ATMC watchdog fault
|  | Bit 3 | = 1 : DYNFCT watchdog fault
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
SF09 |  |  | Safety Mc Auto Test fault register
|  | Bit 0 | Reserved
|  | Bit 1 | = 1 : Ram stack overflow
|  | Bit 2 | = 1 : Ram address integrity error
|  | Bit 3 | = 1 : Ram data access error
|  | Bit 4 | = 1 : Flash Checksum Error
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | = 1 : 1ms task overflow
|  | Bit 10 | = 1 : PWM task overflow
|  | Bit 11 | = 1 : Fixed task overflow
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | = 1 : Unwanted interruption
|  | Bit 15 | = 1 : Hardware WD is not running after initialization
SF10 |  |  | Safety Mc Direct shortcircuit fault register
|  | Bit 0 | = 1 : Ground short circuit - Configuration error
|  | Bit 1 | = 1 : Phase to phase short circuit - Configuration error
|  | Bit 2 | = 1 : Ground short circuit detected
|  | Bit 3 | = 1 : Phase to phase short circuit detected
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
SF11 |  |  | Safety Mc Dynamic check of activity fault register
|  | Bit 0 | = 1 : App requested safe diagnostic of direct short circuit
|  | Bit 1 | = 1 : App requested consistency check of stator frequency estimation (voltage + current)
|  | Bit 2 | = 1 : App requested diagnostic of SpdStat provided by Mc
|  | Bit 3 | Reserved
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | = 1 : MC safe diagnostic of direct short circuit is enabled
|  | Bit 9 | = 1 : Mc consistency check of stator frequency estimation is enabled
|  | Bit 10 | = 1 : Mc diagnostic of SpdStat provided by Mc is enabled
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
UNT | *** UNT should be read after value parameter (APH, PTH, RTH) ***
|  | Bit 0 to 1 | : APH unit (0 : Wh, 1 : kWh, 2 : MWh)
|  | Bit 2 to 3 | : PTH unit (0 : s, 1 : mn, 2 : h)
|  | Bit 4 to 5 | : RTH unit (0 : s, 1 : mn, 2 : h)
|  | Bit 6 | : Reserved
|  | Bit 7 | : Reserved
|  | Bit 8 | : Reserved
|  | Bit 9 | : Reserved
|  | Bit 10 | : Reserved
|  | Bit 11 | : Reserved
|  | Bit 12 | : Reserved
|  | Bit 13 | : Reserved
|  | Bit 14 | : Reserved
|  | Bit 15 | : Reserved